## N2O Emission- Bottom Aeration
Unisense Environment A/S - 2025 ©
Input
Calculations
Constants
| Constant name | Unit | Note | Value | Convert air flow at process temperature
| KHꝊ | mol/L.bar |  | 0.0247 | Choose the air flow type in the Drop down menu
| -ΔsolNH/R | K |  | 2675 | Q_A (Nm3/h) | Nm3/h -DIN 1343 | Air flow in normal cubic meter (STD) | 1000
| CN2O,air | gN/m3 |  | 0.0003 | Q_A [m3/h] | m3/h | Actual air flow rate (V2) | 1073.0276
| R | m3·bar/mol·K |  | 8.314e-05
| kLaNon-aerated process | day-1 | 2-4 day-1 | 3 | There are 2 standards with the same STD pressure and RH=0%, but different temperatures:
| TꝊ | °C | Standard temperature | 25
| Tprocess | °C | Process temperature measured | 15 | DIN 1343 : temperature 273.15K (0°C)
| Pprocess | bar | Pressure in process | 1.013 | ISO 2533 : temperature 288.15K (15°C)
| Aerated zones | Unit | Note | Value
| SN2O concentration | mg N-N2O/L | Nitrous Oxide measured Aerated | 0.5 | In our experience most professionals are using the DIN 1343 but you should always check your own system.
| QA per day (@Tprocess) | m3/day |  | 25752.6626
| QA per second (@ Tprocess) | m3/s |  | 0.29806
| QA per second (@20°C) | m3/s | at 20 deg | 0.30518 | The combined gas law:
| Aerated field size | m2 | Air diffuser cylindrical total area | 1000
| DR | m | Depth reactor from diffuser to water level | 5.2
| VR | m3 | Volume of aerated part of the reactor | 5200 | Constants - This example will use DIN 1343
| Non-aerated zones | Unit | Note | Value | P1 | bar | Standard - DIN 1343 | 1.013
| SN2O concentration | mg N-N2O/L | Nitrous Oxide measured Non-Aerated | 0.25 | T1 | K | Standard - DIN 1343 | 273.15
| Non-aerated field size | m2 | Total area of non-aeration | 600 | T2 | K | Process temperature | 288.15
| DR,Non-aerated | m | Depth reactor | 5.2
| VR,Non-aerated | m3 | Volume of non-aerated part of the reactor | 3120 | For P2 you will have to consider the water vaper pressure, which is temperature dependent.
Formula | Variables on T and air flow | Unit | Note | Value | Campbells equation:
4.2 | KH | mol/L.bar | Henrys constant at the std. Temp. | 0.033723
4.1 | HN2O,Tprocess | dimensionless | Henrys constant | 1.2378 | The combined gas law including Campbells equation
1.1 | Vg | m3/m2/s | Gas velocity | 0.00030518
1.3 | KLaN2O 20°C | day-1 | Mass transfer coefficient at std. Temp | 13.1875
1.4 | KLaN2O Tprocess | day-1 | Mass transfer coefficient at process Temp | 11.7128
Formula | Aerated zone |  |  |  | Water vapor pressure | mbar | Tprocess | 17.0995
2 | rN2O,Tprocess | gN-N2O/m3/day | N2O emission rate | 2.6115 | P2 (@ Tprocess) | bar | Tprocess | 0.9959
| Emission | KgN-N2O/day | N2O emission rate | 13.5798 | Water vapor pressure | mbar | T20°C | 23.4428
[5 empty] | P2 (@20°C) | bar | T20°C | 0.98956
Formula | Non-aerated zone
3 | rN2O,Tprocess | gN-N2O/m3/day | N2O emission rate | 0.74927
| Emission | kgN-N2O/day | N2O emission rate | 2.3377
|  | Total tank emission | kgN-N2O/day | 15.9175
Calculation example on converting N2O emission to CO2-eq
You should now sum up your emission rate using e.g. numerical integration.
|  | Total emission | kgN-N2O | 50.6
Constants
|  | IPCC | kg CO2-eq pr. kg N2O | 273
|  | Atomic mass Nitrogen | mol/L | 14
|  | Atomic mass Oxygen | mol/L | 16
The N2O sensor is measuring the nitrogen in N2O, why you have to calculate the weight of the total molecule N2O.
|  | Weight of N2O molecule | kg-N2O | 79.5143
|  | CO2 equivalent | kg CO2-eq | 21707.4
𝑃_1∗𝑉_1/𝑇_1 =𝑃_2∗𝑉_2/𝑇_2 " "
𝑃_𝑤 (𝑇)=𝑒^(52,57−6690,9/(𝑇+273,15)−4,681∗ln⁡(𝑇+273,15) )
𝑉_2=𝑉_1∗𝑃_1/𝑃_(2,𝑝𝑟𝑜𝑐𝑒𝑠𝑠) ∗𝑇_2/𝑇_1 =𝑉_1∗𝑃_1/(𝑃_𝑝𝑟𝑜𝑐𝑒𝑠𝑠−𝑃_𝑊 (𝑇)[𝑏𝑎𝑟] )∗𝑇_2/𝑇_1

## N2O Emission - Surface Aeration
Input
Calculations
Constants
Method 1
| Constant name | Unit | Note | Value
| Tprocess | °C | Process temperature measured | 15
| P | kWh | Power consumption (rotors) | 37.5
| SAE | kgO2/kWh | Standard aeration efficiency | 1.2
| Vaerated | m3 | Volume of process tank | 1250
| CN2OProcess | mgN-N2O/L = gN-N2O/m3 | Nitrous oxide liquid phase concentration | 0.1
| Non-aerated zones | Unit | Note | Value
| CN2O,non-aeratedProcess | mgN-N2O/L = gN-N2O/m3 | Nitrous oxide liquid phase concentration | 0.01
| kLaNon-aerated process | day-1 | 2-4 day-1 | 3
| Non-aerated field size | m2 | Total area of non-aeration | 162
| DR,Non-aerated | m | Depth reactor | 5.5
| VR,Non-aerated | m3 | Volume of non-aerated part of the reactor | 891
| Constant name | Unit | Note | Value
| TꝊ | °C | Standard temperature | 20
| α | (-) | Correction from clean water to process conditions | 0.9
| β | (-) | Change in saturation concentration from clean water to process conditions | 0.95
| F | (-) | Fouling factor, usually 1 for surface aerator rotors | 1
| DN2O | m2/s | Diffusion coefficient | 1.77e-09
| DO2 | m2/s | Diffusion coefficient | 2.12e-09
| CO2Process | mg/L | Oxygen Process Concentration | 1.5
| CO2Sat(20°C) | kg/m3 | Oxygen Saturation Concentration | 0.0090324
| CO2Sat_Tprocess | kgO2/m3 | Oxygen Saturation Concentration | 0.0098651
Formula | Aerated zone
1.4 | SOTR | kgO2/h | Standard oxygen transfer rate | 45
1.5 | AOTR | kgO2/h | Actual Oxygen Transfer Rate | -5936.3761
1.6 | KLaO2 Tprocess | h-1 | Mass transfer coefficient | 3.187 | 76.4887
0.2 | KLaN2O Tprocess | h-1 | Mass transfer coefficient | 2.9121 | 69.8901
0.4 | NTRAerated | gN-N2O/h | N2O Emission rate | 364.011
| Emission | kgN-N2O/day | N2O Emission rate | 8.7363
Formula | Non-erated zone
0.5 | Emission | kgN-N2O/day | N2O Emission rate | 0.02673
| Total tank emission | kgN-N2O/day | N2O Emission rate | 8.763