## Time series calculation
Site-specific settings
Aerated field size | Air diffuser cylindrical total area | 462 | m2 |  |  |  |  | Input
DR | Depth reactor from diffuser to water level | 7.55 | m |  |  |  |  | Calculations
VR | Volume of aerated part of the reactor | 3488.1 | m3 |  |  |  |  | Constant
Pprocess | Total pressure in process | 1.0132 | bar | If not measured, use 1.013 bar
TNormal | Temperature at normalised airflow reference conditions. | 0 | °C | DIN 1343: temperature 0°C (273.15K); ISO 2533: temperature 15°C (288.15K); It may also be customised to 20°C (293.15K) depending on the case-specific settings.
RHNormal | The relative humidity at normalised airflow reference conditions. | 0 | % | Enter the value before the % sign (e.g., for 20%, enter ‘20’)
PNormal | Gas pressure excluding water vapour at normalised airflow reference conditions. | 1.0132 | bar
P20 | Gas pressure excluding water vapour pressure at 20°C | 0.98981 | bar | This pressure is assumed under 100% RH
Choose the air flow type in the Drop down menu
Normalised Q_A (Nm3/s)
Date_Time | QA per second (@ Monitored) | QA per second (@ Tprocess) | Tprocess | SN2O concentration | PTprocess | QA per second (@20°C) | Vg | QA per day (@Tprocess) | KH | HN2O,Tprocess | KLaN2O 20°C | KLaN2O Tprocess | Emission | Flux
| m3/s | m3/s | °C | mg N-N2O/L | bar | m3/s | m3/m2/s | m3/day | mol/L.bar | dimensionless | day-1 | day-1 | kgN-N2O/day | gN-N2O/h-m2
2025-02-06 | 0.4189 | 0.47566 | 26.431 | 0.041505 | 0.97868 | 0.46022 | 0.00099614 | 41097.014 | 0.023664 | 1.6966 | 30.3842 | 35.3906 | 2.4013 | 0.21656
2025-02-06 00:01 | 0.38917 | 0.4419 | 26.4302 | 0.04146 | 0.97868 | 0.42756 | 0.00092545 | 38180.2771 | 0.023664 | 1.6966 | 28.5203 | 33.2189 | 2.2367 | 0.20172
2025-02-06 00:02 | 0.38917 | 0.4419 | 26.4299 | 0.041454 | 0.97868 | 0.42756 | 0.00092545 | 38180.2102 | 0.023665 | 1.6966 | 28.5203 | 33.2187 | 2.2363 | 0.20169
2025-02-06 00:03 | 0.38917 | 0.4419 | 26.4295 | 0.041549 | 0.97868 | 0.42756 | 0.00092545 | 38180.1467 | 0.023665 | 1.6966 | 28.5203 | 33.2184 | 2.2415 | 0.20215
2025-02-06 00:04 | 0.39303 | 0.44628 | 26.4292 | 0.041578 | 0.97869 | 0.4318 | 0.00093463 | 38558.8554 | 0.023665 | 1.6966 | 28.7635 | 33.5014 | 2.2641 | 0.2042
2025-02-06 00:05 | 0.38878 | 0.44146 | 26.4289 | 0.041552 | 0.97869 | 0.42713 | 0.00092453 | 38142.1463 | 0.023665 | 1.6966 | 28.496 | 33.1896 | 2.2395 | 0.20197
2025-02-06 00:06 | 0.40616 | 0.46119 | 26.4286 | 0.04153 | 0.97869 | 0.44622 | 0.00096584 | 39846.5443 | 0.023665 | 1.6965 | 29.5878 | 34.4609 | 2.3331 | 0.21042
2025-02-06 00:07 | 0.41272 | 0.46864 | 26.4283 | 0.041594 | 0.97869 | 0.45343 | 0.00098145 | 40490.3843 | 0.023666 | 1.6965 | 29.9985 | 34.939 | 2.3725 | 0.21397
2025-02-06 00:08 | 0.3633 | 0.41252 | 26.4282 | 0.041562 | 0.97869 | 0.39914 | 0.00086393 | 35642.116 | 0.023666 | 1.6965 | 26.8823 | 31.3095 | 2.1002 | 0.18942
2025-02-06 00:09 | 0.36794 | 0.41779 | 26.4284 | 0.041454 | 0.97869 | 0.40423 | 0.00087495 | 36096.6775 | 0.023666 | 1.6965 | 27.1768 | 31.6527 | 2.1202 | 0.19121
2025-02-06 00:10 | 0.37257 | 0.42305 | 26.4286 | 0.041482 | 0.97869 | 0.40932 | 0.00088597 | 36551.2431 | 0.023666 | 1.6965 | 27.4709 | 31.9953 | 2.147 | 0.19363
2025-02-06 00:11 | 0.37527 | 0.42612 | 26.4288 | 0.041501 | 0.97869 | 0.41229 | 0.0008924 | 36816.4254 | 0.023665 | 1.6965 | 27.6421 | 32.195 | 2.1628 | 0.19506
2025-02-06 00:12 | 0.36948 | 0.41954 | 26.429 | 0.041552 | 0.97869 | 0.40592 | 0.00087862 | 36248.3125 | 0.023665 | 1.6966 | 27.2749 | 31.7674 | 2.1337 | 0.19244
2025-02-06 00:13 | 0.37102 | 0.42129 | 26.4291 | 0.04153 | 0.97869 | 0.40762 | 0.0008823 | 36399.8365 | 0.023665 | 1.6966 | 27.3729 | 31.8816 | 2.1411 | 0.1931
2025-02-06 00:14 | 0.38261 | 0.43445 | 26.4289 | 0.041638 | 0.97869 | 0.42035 | 0.00090984 | 37536.1053 | 0.023665 | 1.6966 | 28.1062 | 32.7355 | 2.2102 | 0.19934
2025-02-06 00:15 | 0.38569 | 0.43795 | 26.4287 | 0.041679 | 0.97869 | 0.42374 | 0.00091718 | 37839.0767 | 0.023665 | 1.6965 | 28.3012 | 32.9625 | 2.2294 | 0.20106
2025-02-06 00:16 | 0.39959 | 0.45373 | 26.4285 | 0.041574 | 0.97869 | 0.43901 | 0.00095024 | 39202.6024 | 0.023666 | 1.6965 | 29.1761 | 33.9813 | 2.2998 | 0.20741
2025-02-06 00:17 | 0.39805 | 0.45198 | 26.4283 | 0.0416 | 0.97869 | 0.43731 | 0.00094656 | 39051.0499 | 0.023666 | 1.6965 | 29.0791 | 33.8682 | 2.2927 | 0.20678
2025-02-06 00:18 | 0.38647 | 0.43883 | 26.428 | 0.041578 | 0.97869 | 0.42459 | 0.00091902 | 37914.6853 | 0.023666 | 1.6965 | 28.3499 | 33.0187 | 2.2281 | 0.20095
2025-02-06 00:19 | 0.38917 | 0.4419 | 26.4275 | 0.041574 | 0.97869 | 0.42756 | 0.00092545 | 38179.7336 | 0.023666 | 1.6965 | 28.5203 | 33.2168 | 2.2427 | 0.20226
2025-02-06 00:20 | 0.37952 | 0.43093 | 26.4271 | 0.041644 | 0.97869 | 0.41695 | 0.00090249 | 37232.7299 | 0.023667 | 1.6965 | 27.911 | 32.5068 | 2.1935 | 0.19783
2025-02-06 00:21 | 0.36987 | 0.41997 | 26.4267 | 0.041673 | 0.97869 | 0.40635 | 0.00087954 | 36285.7315 | 0.023667 | 1.6965 | 27.2994 | 31.7942 | 2.1419 | 0.19317
2025-02-06 00:22 | 0.38299 | 0.43488 | 26.4263 | 0.041625 | 0.97869 | 0.42077 | 0.00091076 | 37573.4467 | 0.023667 | 1.6964 | 28.1306 | 32.7619 | 2.2115 | 0.19945
2025-02-06 00:23 | 0.39187 | 0.44496 | 26.4256 | 0.041622 | 0.97869 | 0.43053 | 0.00093187 | 38444.4594 | 0.023668 | 1.6964 | 28.6906 | 33.4136 | 2.26 | 0.20382
2025-02-06 00:24 | 0.38338 | 0.43531 | 26.4243 | 0.041603 | 0.9787 | 0.42119 | 0.00091168 | 37610.9224 | 0.023669 | 1.6963 | 28.155 | 32.7888 | 2.2123 | 0.19952
2025-02-06 00:25 | 0.37334 | 0.42391 | 26.423 | 0.041552 | 0.9787 | 0.41017 | 0.00088781 | 36625.8908 | 0.023669 | 1.6963 | 27.5198 | 32.0481 | 2.1545 | 0.19431
2025-02-06 00:26 | 0.40152 | 0.45591 | 26.4217 | 0.041597 | 0.9787 | 0.44113 | 0.00095483 | 39390.5484 | 0.02367 | 1.6962 | 29.2973 | 34.117 | 2.3111 | 0.20843
2025-02-06 00:27 | 0.43511 | 0.49404 | 26.4204 | 0.041625 | 0.9787 | 0.47803 | 0.0010347 | 42685.4225 | 0.023671 | 1.6962 | 31.393 | 36.5564 | 2.4959 | 0.2251
2025-02-06 00:28 | 0.40423 | 0.45897 | 26.4196 | 0.041578 | 0.9787 | 0.4441 | 0.00096125 | 39655.2224 | 0.023672 | 1.6961 | 29.4668 | 34.3127 | 2.3247 | 0.20966
2025-02-06 00:29 | 0.37411 | 0.42478 | 26.4198 | 0.041552 | 0.9787 | 0.41101 | 0.00088964 | 36701.0002 | 0.023672 | 1.6961 | 27.5688 | 32.1026 | 2.1586 | 0.19468
2025-02-06 00:30 | 0.35828 | 0.40681 | 26.42 | 0.041552 | 0.9787 | 0.39362 | 0.000852 | 35148.1613 | 0.023672 | 1.6962 | 26.5626 | 30.9311 | 2.0717 | 0.18684
2025-02-06 00:31 | 0.35906 | 0.40768 | 26.4202 | 0.041619 | 0.9787 | 0.39447 | 0.00085384 | 35223.953 | 0.023671 | 1.6962 | 26.6118 | 30.9886 | 2.0793 | 0.18753
2025-02-06 00:32 | 0.38299 | 0.43486 | 26.4204 | 0.04174 | 0.9787 | 0.42077 | 0.00091076 | 37572.2604 | 0.023671 | 1.6962 | 28.1306 | 32.7574 | 2.2172 | 0.19996
2025-02-06 00:33 | 0.38608 | 0.43837 | 26.4207 | 0.041679 | 0.9787 | 0.42416 | 0.0009181 | 37875.3063 | 0.023671 | 1.6962 | 28.3256 | 32.9846 | 2.231 | 0.20121
2025-02-06 00:34 | 0.36369 | 0.41295 | 26.4209 | 0.041574 | 0.9787 | 0.39956 | 0.00086485 | 35678.5804 | 0.023671 | 1.6962 | 26.9068 | 31.3327 | 2.1026 | 0.18963
2025-02-06 00:35 | 0.35326 | 0.40111 | 26.4211 | 0.0418 | 0.9787 | 0.38811 | 0.00084006 | 34655.9856 | 0.023671 | 1.6962 | 26.2422 | 30.5589 | 2.0564 | 0.18546
2025-02-06 00:36 | 0.35944 | 0.40813 | 26.4213 | 0.041851 | 0.9787 | 0.3949 | 0.00085475 | 35262.0327 | 0.023671 | 1.6962 | 26.6364 | 31.0181 | 2.0931 | 0.18877
2025-02-06 00:37 | 0.36253 | 0.41163 | 26.4215 | 0.041692 | 0.9787 | 0.39829 | 0.0008621 | 35565.0769 | 0.023671 | 1.6962 | 26.8331 | 31.2473 | 2.1022 | 0.18959
2025-02-06 00:38 | 0.3745 | 0.42522 | 26.4214 | 0.04181 | 0.9787 | 0.41144 | 0.00089056 | 36739.1945 | 0.023671 | 1.6962 | 27.5932 | 32.1324 | 2.1742 | 0.19608
2025-02-06 00:39 | 0.37411 | 0.42478 | 26.4206 | 0.041797 | 0.9787 | 0.41101 | 0.00088964 | 36701.1531 | 0.023671 | 1.6962 | 27.5688 | 32.1032 | 2.1713 | 0.19583
2025-02-06 00:40 | 0.34863 | 0.39585 | 26.4197 | 0.041695 | 0.9787 | 0.38302 | 0.00082905 | 34201.2257 | 0.023672 | 1.6961 | 25.946 | 30.2129 | 2.0255 | 0.18268
2025-02-06 00:41 | 0.33782 | 0.38357 | 26.4188 | 0.041629 | 0.97871 | 0.37114 | 0.00080334 | 33140.5679 | 0.023672 | 1.6961 | 25.2526 | 29.4049 | 1.9626 | 0.177
2025-02-06 00:42 | 0.3606 | 0.40943 | 26.418 | 0.041552 | 0.97871 | 0.39617 | 0.00085751 | 35375.0246 | 0.023673 | 1.6961 | 26.7102 | 31.1016 | 2.0843 | 0.18798
2025-02-06 00:43 | 0.36794 | 0.41776 | 26.4173 | 0.041552 | 0.97871 | 0.40423 | 0.00087495 | 36094.5033 | 0.023674 | 1.696 | 27.1768 | 31.6443 | 2.1245 | 0.19161
2025-02-06 00:44 | 0.37257 | 0.42302 | 26.4168 | 0.041641 | 0.97871 | 0.40932 | 0.00088597 | 36548.9123 | 0.023674 | 1.696 | 27.4709 | 31.9864 | 2.1545 | 0.19431
2025-02-06 00:45 | 0.38492 | 0.43705 | 26.4164 | 0.041632 | 0.97871 | 0.42289 | 0.00091535 | 37760.8101 | 0.023674 | 1.696 | 28.2525 | 32.8962 | 2.2218 | 0.20038
2025-02-06 00:46 | 0.39264 | 0.44581 | 26.416 | 0.041527 | 0.97871 | 0.43137 | 0.00093371 | 38518.2088 | 0.023674 | 1.696 | 28.7392 | 33.4625 | 2.2584 | 0.20368
2025-02-06 00:47 | 0.3884 | 0.44099 | 26.4155 | 0.041552 | 0.97871 | 0.42671 | 0.00092361 | 38101.5016 | 0.023675 | 1.696 | 28.4717 | 33.1507 | 2.2365 | 0.20171
2025-02-06 00:48 | 0.38029 | 0.43178 | 26.4149 | 0.041552 | 0.97871 | 0.4178 | 0.00090433 | 37306.0156 | 0.023675 | 1.6959 | 27.9598 | 32.5542 | 2.1921 | 0.1977
2025-02-06 00:49 | 0.37102 | 0.42126 | 26.4138 | 0.041552 | 0.97872 | 0.40762 | 0.0008823 | 36396.8282 | 0.023676 | 1.6959 | 27.3729 | 31.8701 | 2.1413 | 0.19311
2025-02-06 00:50 | 0.3884 | 0.44098 | 26.4128 | 0.041619 | 0.97872 | 0.42671 | 0.00092361 | 38100.9323 | 0.023677 | 1.6958 | 28.4717 | 33.1485 | 2.2399 | 0.20201
2025-02-06 00:51 | 0.38994 | 0.44273 | 26.4117 | 0.041629 | 0.97872 | 0.42841 | 0.00092728 | 38252.2046 | 0.023677 | 1.6958 | 28.569 | 33.261 | 2.2488 | 0.20282
2025-02-06 00:52 | 0.37682 | 0.42783 | 26.4106 | 0.041619 | 0.97872 | 0.41398 | 0.00089607 | 36964.292 | 0.023678 | 1.6957 | 27.7399 | 32.295 | 2.1763 | 0.19627
2025-02-06 00:53 | 0.37373 | 0.42432 | 26.4097 | 0.041584 | 0.97872 | 0.41059 | 0.00088872 | 36661.1189 | 0.023679 | 1.6957 | 27.5443 | 32.0665 | 2.1575 | 0.19458
2025-02-06 00:54 | 0.38454 | 0.43659 | 26.409 | 0.041501 | 0.97873 | 0.42247 | 0.00091443 | 37721.4313 | 0.023679 | 1.6957 | 28.2281 | 32.862 | 2.2123 | 0.19952
2025-02-06 00:55 | 0.3884 | 0.44097 | 26.4084 | 0.04153 | 0.97873 | 0.42671 | 0.00092361 | 38100.0273 | 0.02368 | 1.6956 | 28.4717 | 33.1451 | 2.2348 | 0.20156
2025-02-06 00:56 | 0.39959 | 0.45368 | 26.4077 | 0.041527 | 0.97873 | 0.43901 | 0.00095024 | 39198.2015 | 0.02368 | 1.6956 | 29.1761 | 33.9646 | 2.2958 | 0.20705
2025-02-06 00:57 | 0.39612 | 0.44974 | 26.4071 | 0.041552 | 0.97873 | 0.43519 | 0.00094197 | 38857.2119 | 0.023681 | 1.6956 | 28.9578 | 33.71 | 2.2782 | 0.20546
2025-02-06 00:58 | 0.38183 | 0.43352 | 26.4065 | 0.041552 | 0.97873 | 0.4195 | 0.000908 | 37455.8089 | 0.023681 | 1.6955 | 28.0574 | 32.6614 | 2.2 | 0.19841
2025-02-06 00:59 | 0.38647 | 0.43878 | 26.4061 | 0.041552 | 0.97873 | 0.42459 | 0.00091902 | 37910.1824 | 0.023681 | 1.6955 | 28.3499 | 33.0015 | 2.2253 | 0.2007
2025-02-06 01:00 | 0.38145 | 0.43308 | 26.4056 | 0.041619 | 0.97873 | 0.41907 | 0.00090709 | 37417.7484 | 0.023682 | 1.6955 | 28.033 | 32.6323 | 2.2014 | 0.19854
2025-02-06 01:01 | 0.38222 | 0.43395 | 26.4051 | 0.041629 | 0.97873 | 0.41992 | 0.00090892 | 37493.4011 | 0.023682 | 1.6955 | 28.0818 | 32.6887 | 2.2061 | 0.19896
2025-02-06 01:02 | 0.42546 | 0.48304 | 26.4047 | 0.04153 | 0.97874 | 0.46743 | 0.0010117 | 41734.9751 | 0.023682 | 1.6955 | 30.7932 | 35.8445 | 2.4366 | 0.21975
2025-02-06 01:03 | 0.42855 | 0.48655 | 26.4042 | 0.041683 | 0.97874 | 0.47082 | 0.0010191 | 42037.8452 | 0.023683 | 1.6954 | 30.9854 | 36.0678 | 2.4623 | 0.22207
2025-02-06 01:04 | 0.39535 | 0.44885 | 26.4038 | 0.04173 | 0.97874 | 0.43434 | 0.00094014 | 38780.7622 | 0.023683 | 1.6954 | 28.9092 | 33.6508 | 2.2835 | 0.20594
2025-02-06 01:05 | 0.39959 | 0.45367 | 26.4035 | 0.041441 | 0.97874 | 0.43901 | 0.00095024 | 39197.2997 | 0.023683 | 1.6954 | 29.1761 | 33.9612 | 2.2907 | 0.2066
2025-02-06 01:06 | 0.38878 | 0.4414 | 26.4037 | 0.041314 | 0.97874 | 0.42713 | 0.00092453 | 38136.9316 | 0.023683 | 1.6954 | 28.496 | 33.1697 | 2.225 | 0.20067
2025-02-06 01:07 | 0.40191 | 0.4563 | 26.4039 | 0.041336 | 0.97874 | 0.44155 | 0.00095574 | 39424.6188 | 0.023683 | 1.6954 | 29.3215 | 34.1308 | 2.2975 | 0.20721
2025-02-06 01:08 | 0.39573 | 0.44929 | 26.4041 | 0.041362 | 0.97874 | 0.43477 | 0.00094106 | 38818.7142 | 0.023683 | 1.6954 | 28.9335 | 33.6793 | 2.2654 | 0.20431
2025-02-06 01:09 | 0.39844 | 0.45236 | 26.4043 | 0.041451 | 0.97874 | 0.43774 | 0.00094748 | 39083.8641 | 0.023683 | 1.6954 | 29.1034 | 33.8772 | 2.285 | 0.20608
2025-02-06 01:10 | 0.39844 | 0.45236 | 26.4042 | 0.041485 | 0.97874 | 0.43774 | 0.00094748 | 39083.8262 | 0.023683 | 1.6954 | 29.1034 | 33.8771 | 2.2869 | 0.20625
2025-02-06 01:11 | 0.39457 | 0.44797 | 26.4031 | 0.041431 | 0.97874 | 0.43349 | 0.0009383 | 38704.8866 | 0.023683 | 1.6954 | 28.8607 | 33.5937 | 2.2629 | 0.20408
2025-02-06 01:12 | 0.37566 | 0.42649 | 26.402 | 0.041501 | 0.97874 | 0.41271 | 0.00089331 | 36848.957 | 0.023684 | 1.6953 | 27.6666 | 32.203 | 2.1633 | 0.1951
2025-02-06 01:13 | 0.35674 | 0.40501 | 26.401 | 0.041485 | 0.97874 | 0.39193 | 0.00084833 | 34993.0512 | 0.023685 | 1.6953 | 26.4641 | 30.8025 | 2.0588 | 0.18567
2025-02-06 01:14 | 0.36832 | 0.41816 | 26.3999 | 0.041387 | 0.97874 | 0.40465 | 0.00087587 | 36128.98 | 0.023686 | 1.6952 | 27.2013 | 31.6599 | 2.1171 | 0.19094
2025-02-06 01:15 | 0.38454 | 0.43657 | 26.3991 | 0.041406 | 0.97875 | 0.42247 | 0.00091443 | 37719.3994 | 0.023686 | 1.6952 | 28.2281 | 32.8543 | 2.2065 | 0.199
2025-02-06 01:16 | 0.38454 | 0.43657 | 26.3989 | 0.041524 | 0.97875 | 0.42247 | 0.00091443 | 37719.3517 | 0.023686 | 1.6952 | 28.2281 | 32.8541 | 2.2128 | 0.19957
2025-02-06 01:17 | 0.37295 | 0.42342 | 26.3986 | 0.041578 | 0.97875 | 0.40974 | 0.00088689 | 36583.1835 | 0.023687 | 1.6952 | 27.4953 | 32.0011 | 2.1522 | 0.1941
2025-02-06 01:18 | 0.36253 | 0.41158 | 26.3984 | 0.041485 | 0.97875 | 0.39829 | 0.0008621 | 35560.6302 | 0.023687 | 1.6952 | 26.8331 | 31.2302 | 2.0904 | 0.18852
2025-02-06 01:19 | 0.3745 | 0.42517 | 26.3982 | 0.041454 | 0.97875 | 0.41144 | 0.00089056 | 36734.5809 | 0.023687 | 1.6952 | 27.5932 | 32.1147 | 2.1542 | 0.19428
2025-02-06 01:20 | 0.38569 | 0.43788 | 26.3978 | 0.04146 | 0.97875 | 0.42374 | 0.00091718 | 37832.7468 | 0.023687 | 1.6952 | 28.3012 | 32.9384 | 2.2157 | 0.19982
2025-02-06 01:21 | 0.39187 | 0.44489 | 26.397 | 0.04152 | 0.97875 | 0.43053 | 0.00093187 | 38438.5008 | 0.023688 | 1.6951 | 28.6906 | 33.3909 | 2.2526 | 0.20315
2025-02-06 01:22 | 0.38145 | 0.43305 | 26.3961 | 0.041603 | 0.97875 | 0.41907 | 0.00090709 | 37415.8246 | 0.023688 | 1.6951 | 28.033 | 32.6249 | 2.1999 | 0.19841
2025-02-06 01:23 | 0.36292 | 0.41201 | 26.3952 | 0.041552 | 0.97875 | 0.39871 | 0.00086302 | 35597.887 | 0.023689 | 1.695 | 26.8577 | 31.2564 | 2.0956 | 0.189
2025-02-06 01:24 | 0.33087 | 0.37563 | 26.3944 | 0.041552 | 0.97876 | 0.36351 | 0.00078681 | 32454.5184 | 0.02369 | 1.695 | 24.8052 | 28.8672 | 1.9193 | 0.1731
2025-02-06 01:25 | 0.3301 | 0.37475 | 26.3937 | 0.04153 | 0.97876 | 0.36266 | 0.00078498 | 32378.6628 | 0.02369 | 1.695 | 24.7554 | 28.8088 | 1.914 | 0.17262
2025-02-06 01:26 | 0.37643 | 0.42735 | 26.3935 | 0.041527 | 0.97876 | 0.41356 | 0.00089515 | 36922.9911 | 0.02369 | 1.695 | 27.7155 | 32.2534 | 2.1683 | 0.19555
2025-02-06 01:27 | 0.38068 | 0.43217 | 26.3933 | 0.041597 | 0.97876 | 0.41823 | 0.00090525 | 37339.5156 | 0.02369 | 1.695 | 27.9842 | 32.5659 | 2.1952 | 0.19798
2025-02-06 01:28 | 0.37527 | 0.42603 | 26.3931 | 0.041648 | 0.97876 | 0.41229 | 0.0008924 | 36809.2976 | 0.023691 | 1.6949 | 27.6421 | 32.1677 | 2.1682 | 0.19554
2025-02-06 01:29 | 0.37527 | 0.42603 | 26.3928 | 0.041648 | 0.97876 | 0.41229 | 0.0008924 | 36809.2548 | 0.023691 | 1.6949 | 27.6421 | 32.1675 | 2.1682 | 0.19554
2025-02-06 01:30 | 0.38299 | 0.4348 | 26.3928 | 0.04167 | 0.97876 | 0.42077 | 0.00091076 | 37566.6291 | 0.023691 | 1.6949 | 28.1306 | 32.7359 | 2.2117 | 0.19947
2025-02-06 01:31 | 0.39766 | 0.45146 | 26.393 | 0.041695 | 0.97876 | 0.43689 | 0.00094565 | 39005.7153 | 0.023691 | 1.6949 | 29.0549 | 33.8116 | 2.2935 | 0.20685
2025-02-06 01:32 | 0.40307 | 0.45759 | 26.3932 | 0.041718 | 0.97876 | 0.44283 | 0.0009585 | 39535.9356 | 0.023691 | 1.6949 | 29.3942 | 34.2067 | 2.3244 | 0.20963
2025-02-06 01:33 | 0.38376 | 0.43568 | 26.3934 | 0.041832 | 0.97876 | 0.42162 | 0.00091259 | 37642.4958 | 0.02369 | 1.695 | 28.1794 | 32.7931 | 2.2246 | 0.20063
2025-02-06 01:34 | 0.37411 | 0.42472 | 26.3936 | 0.041822 | 0.97876 | 0.41101 | 0.00088964 | 36695.7967 | 0.02369 | 1.695 | 27.5688 | 32.0827 | 2.171 | 0.19579
2025-02-06 01:35 | 0.41195 | 0.46767 | 26.3936 | 0.041718 | 0.97876 | 0.45258 | 0.00097962 | 40407.0361 | 0.02369 | 1.695 | 29.9502 | 34.8541 | 2.373 | 0.21401
2025-02-06 01:36 | 0.4077 | 0.46285 | 26.3932 | 0.041721 | 0.97876 | 0.44792 | 0.00096952 | 39990.3722 | 0.023691 | 1.6949 | 29.6845 | 34.5445 | 2.3499 | 0.21193
2025-02-06 01:37 | 0.38106 | 0.43261 | 26.3927 | 0.04174 | 0.97876 | 0.41865 | 0.00090617 | 37377.271 | 0.023691 | 1.6949 | 28.0086 | 32.5939 | 2.2048 | 0.19885
2025-02-06 01:38 | 0.38338 | 0.43524 | 26.3923 | 0.041679 | 0.97876 | 0.42119 | 0.00091168 | 37604.3942 | 0.023691 | 1.6949 | 28.155 | 32.7639 | 2.2143 | 0.1997
2025-02-06 01:39 | 0.39264 | 0.44575 | 26.3918 | 0.041552 | 0.97876 | 0.43137 | 0.00093371 | 38513.1671 | 0.023691 | 1.6949 | 28.7392 | 33.4434 | 2.2582 | 0.20366
2025-02-06 01:40 | 0.41697 | 0.47337 | 26.3913 | 0.041619 | 0.97876 | 0.4581 | 0.00099155 | 40898.8356 | 0.023692 | 1.6949 | 30.2638 | 35.2171 | 2.3946 | 0.21596
2025-02-06 01:41 | 0.43434 | 0.49309 | 26.3909 | 0.04174 | 0.97876 | 0.47718 | 0.0010329 | 42602.8469 | 0.023692 | 1.6948 | 31.3451 | 36.475 | 2.4964 | 0.22514
2025-02-06 01:42 | 0.42199 | 0.47906 | 26.3908 | 0.041768 | 0.97876 | 0.46361 | 0.0010035 | 41391.0049 | 0.023692 | 1.6948 | 30.5768 | 35.5809 | 2.4306 | 0.21921
2025-02-06 01:43 | 0.36485 | 0.4142 | 26.3914 | 0.041698 | 0.97876 | 0.40083 | 0.00086761 | 35786.4884 | 0.023692 | 1.6949 | 26.9805 | 31.3965 | 2.1134 | 0.1906
2025-02-06 01:44 | 0.33164 | 0.3765 | 26.392 | 0.041625 | 0.97876 | 0.36436 | 0.00078865 | 32529.8425 | 0.023691 | 1.6949 | 24.8549 | 28.9235 | 1.9268 | 0.17377
2025-02-06 01:45 | 0.34284 | 0.38921 | 26.3927 | 0.041644 | 0.97876 | 0.37666 | 0.00081528 | 33628.1746 | 0.023691 | 1.6949 | 25.5749 | 29.7617 | 1.9895 | 0.17943
2025-02-06 01:46 | 0.3884 | 0.44094 | 26.3933 | 0.041829 | 0.97876 | 0.42671 | 0.00092361 | 38096.9169 | 0.02369 | 1.695 | 28.4717 | 33.1332 | 2.2499 | 0.20292
2025-02-06 01:47 | 0.35365 | 0.40149 | 26.3937 | 0.041848 | 0.97876 | 0.38853 | 0.00084098 | 34688.7081 | 0.02369 | 1.695 | 26.2669 | 30.5677 | 2.0592 | 0.18572
2025-02-06 01:48 | 0.34091 | 0.38702 | 26.3934 | 0.041784 | 0.97876 | 0.37454 | 0.00081068 | 33438.9535 | 0.02369 | 1.695 | 25.451 | 29.618 | 1.9856 | 0.17907
2025-02-06 01:49 | 0.34014 | 0.38615 | 26.3931 | 0.041708 | 0.97876 | 0.37369 | 0.00080885 | 33363.1588 | 0.023691 | 1.6949 | 25.4014 | 29.5601 | 1.9777 | 0.17836
2025-02-06 01:50 | 0.32547 | 0.36949 | 26.3928 | 0.041459 | 0.97876 | 0.35757 | 0.00077396 | 31924.0588 | 0.023691 | 1.6949 | 24.4563 | 28.46 | 1.8851 | 0.17002
2025-02-06 01:51 | 0.30114 | 0.34188 | 26.3925 | 0.041524 | 0.97876 | 0.33085 | 0.00071612 | 29538.2258 | 0.023691 | 1.6949 | 22.876 | 26.6209 | 1.7536 | 0.15815
2025-02-06 01:52 | 0.32624 | 0.37037 | 26.3921 | 0.041694 | 0.97876 | 0.35842 | 0.0007758 | 31999.6918 | 0.023691 | 1.6949 | 24.5062 | 28.5177 | 1.9 | 0.17136
2025-02-06 01:53 | 0.36716 | 0.41683 | 26.3918 | 0.041651 | 0.97876 | 0.40338 | 0.00087312 | 36013.7954 | 0.023691 | 1.6949 | 27.1278 | 31.5682 | 2.1238 | 0.19154
2025-02-06 01:54 | 0.34825 | 0.39535 | 26.3916 | 0.041621 | 0.97876 | 0.3826 | 0.00082813 | 34158.1559 | 0.023692 | 1.6949 | 25.9213 | 30.1641 | 2.0182 | 0.18201
2025-02-06 01:55 | 0.32778 | 0.37212 | 26.3916 | 0.041764 | 0.97876 | 0.36011 | 0.00077947 | 32151.0779 | 0.023692 | 1.6949 | 24.6059 | 28.6334 | 1.9118 | 0.17242
2025-02-06 01:56 | 0.36755 | 0.41726 | 26.3916 | 0.041838 | 0.97876 | 0.4038 | 0.00087403 | 36051.6207 | 0.023692 | 1.6949 | 27.1523 | 31.5966 | 2.1354 | 0.19259
2025-02-06 01:57 | 0.3911 | 0.444 | 26.3916 | 0.041792 | 0.97876 | 0.42968 | 0.00093004 | 38361.6511 | 0.023692 | 1.6949 | 28.642 | 33.3301 | 2.2627 | 0.20407
2025-02-06 01:58 | 0.38801 | 0.44049 | 26.3916 | 0.041766 | 0.97876 | 0.42628 | 0.00092269 | 38058.6969 | 0.023692 | 1.6949 | 28.4473 | 33.1036 | 2.2443 | 0.20241
2025-02-06 01:59 | 0.37797 | 0.4291 | 26.3916 | 0.041652 | 0.97876 | 0.41526 | 0.00089882 | 37074.0944 | 0.023692 | 1.6949 | 27.8133 | 32.3657 | 2.1832 | 0.1969
2025-02-06 02:00 | 0.37141 | 0.42165 | 26.3916 | 0.041666 | 0.97876 | 0.40805 | 0.00088321 | 36430.3164 | 0.023692 | 1.6949 | 27.3974 | 31.8818 | 2.1479 | 0.19371
2025-02-06 02:01 | 0.39882 | 0.45277 | 26.3914 | 0.041746 | 0.97876 | 0.43816 | 0.0009484 | 39118.9965 | 0.023692 | 1.6949 | 29.1276 | 33.8951 | 2.3026 | 0.20766
2025-02-06 02:02 | 0.4216 | 0.47862 | 26.3908 | 0.041694 | 0.97876 | 0.46319 | 0.0010026 | 41353.1436 | 0.023692 | 1.6948 | 30.5527 | 35.5529 | 2.4241 | 0.21863
2025-02-06 02:03 | 0.37373 | 0.42427 | 26.3901 | 0.041628 | 0.97876 | 0.41059 | 0.00088872 | 36657.2361 | 0.023693 | 1.6948 | 27.5443 | 32.0516 | 2.1585 | 0.19467
2025-02-06 02:04 | 0.34631 | 0.39315 | 26.3895 | 0.041528 | 0.97877 | 0.38047 | 0.00082354 | 33968.4166 | 0.023693 | 1.6948 | 25.7977 | 30.0187 | 2.0029 | 0.18064
2025-02-06 02:05 | 0.32855 | 0.37299 | 26.3889 | 0.041621 | 0.97877 | 0.36096 | 0.00078131 | 32226.3349 | 0.023694 | 1.6948 | 24.6557 | 28.6895 | 1.9094 | 0.1722
2025-02-06 02:06 | 0.33049 | 0.37518 | 26.3885 | 0.041626 | 0.97877 | 0.36308 | 0.0007859 | 32415.61 | 0.023694 | 1.6947 | 24.7803 | 28.8341 | 1.9202 | 0.17318
2025-02-06 02:07 | 0.35983 | 0.40849 | 26.3886 | 0.041598 | 0.97877 | 0.39532 | 0.00085567 | 35293.6573 | 0.023694 | 1.6947 | 26.661 | 31.0226 | 2.0806 | 0.18764
2025-02-06 02:08 | 0.36485 | 0.41419 | 26.3888 | 0.041602 | 0.97877 | 0.40083 | 0.00086761 | 35785.9805 | 0.023694 | 1.6947 | 26.9805 | 31.3945 | 2.1083 | 0.19015
2025-02-06 02:09 | 0.35867 | 0.40718 | 26.3889 | 0.041644 | 0.97877 | 0.39405 | 0.00085292 | 35180.1098 | 0.023694 | 1.6948 | 26.5872 | 30.937 | 2.0765 | 0.18728
2025-02-06 02:10 | 0.34593 | 0.39271 | 26.3891 | 0.04172 | 0.97877 | 0.38005 | 0.00082262 | 33930.4685 | 0.023693 | 1.6948 | 25.7729 | 29.9896 | 2.01 | 0.18128
2025-02-06 02:11 | 0.31659 | 0.3594 | 26.3892 | 0.041625 | 0.97877 | 0.34781 | 0.00075284 | 31052.4629 | 0.023693 | 1.6948 | 23.8813 | 27.7886 | 1.8433 | 0.16624
2025-02-06 02:12 | 0.32701 | 0.37124 | 26.3894 | 0.041719 | 0.97877 | 0.35927 | 0.00077763 | 32074.9483 | 0.023693 | 1.6948 | 24.556 | 28.5738 | 1.9053 | 0.17184
2025-02-06 02:13 | 0.37025 | 0.42033 | 26.3892 | 0.041838 | 0.97877 | 0.40677 | 0.00088046 | 36316.2271 | 0.023693 | 1.6948 | 27.3239 | 31.7944 | 2.1502 | 0.19392
2025-02-06 02:14 | 0.38724 | 0.43961 | 26.3883 | 0.041719 | 0.97877 | 0.42544 | 0.00092086 | 37982.2841 | 0.023694 | 1.6947 | 28.3986 | 33.0444 | 2.2374 | 0.20178
2025-02-06 02:15 | 0.37488 | 0.42558 | 26.3875 | 0.0416 | 0.97877 | 0.41186 | 0.00089148 | 36770.317 | 0.023695 | 1.6947 | 27.6177 | 32.135 | 2.1633 | 0.1951
2025-02-06 02:16 | 0.36523 | 0.41462 | 26.3866 | 0.041695 | 0.97877 | 0.40126 | 0.00086853 | 35823.4376 | 0.023695 | 1.6947 | 27.0051 | 31.4215 | 2.1151 | 0.19075
2025-02-06 02:17 | 0.37064 | 0.42076 | 26.3858 | 0.041576 | 0.97877 | 0.4072 | 0.00088138 | 36353.4247 | 0.023696 | 1.6946 | 27.3484 | 31.8204 | 2.1386 | 0.19288
2025-02-06 02:18 | 0.35519 | 0.40322 | 26.3851 | 0.041433 | 0.97877 | 0.39023 | 0.00084465 | 34838.5769 | 0.023696 | 1.6946 | 26.3655 | 30.6763 | 2.0468 | 0.18459
2025-02-06 02:19 | 0.3413 | 0.38745 | 26.3849 | 0.041481 | 0.97878 | 0.37496 | 0.0008116 | 33475.287 | 0.023696 | 1.6946 | 25.4758 | 29.6409 | 1.9728 | 0.17792
2025-02-06 02:20 | 0.35018 | 0.39753 | 26.3847 | 0.041433 | 0.97878 | 0.38472 | 0.00083272 | 34346.2108 | 0.023697 | 1.6946 | 26.0448 | 30.3028 | 2.0192 | 0.18211
2025-02-06 02:21 | 0.34554 | 0.39227 | 26.3845 | 0.041481 | 0.97878 | 0.37963 | 0.0008217 | 33891.7567 | 0.023697 | 1.6946 | 25.7482 | 29.9576 | 1.9961 | 0.18002
2025-02-06 02:22 | 0.34863 | 0.39577 | 26.3843 | 0.041552 | 0.97878 | 0.38302 | 0.00082905 | 34194.6597 | 0.023697 | 1.6945 | 25.946 | 30.1875 | 2.0165 | 0.18186
2025-02-06 02:23 | 0.36639 | 0.41593 | 26.3841 | 0.041505 | 0.97878 | 0.40253 | 0.00087128 | 35936.5518 | 0.023697 | 1.6945 | 27.0787 | 31.5053 | 2.1116 | 0.19044
2025-02-06 02:24 | 0.37797 | 0.42908 | 26.3841 | 0.041505 | 0.97878 | 0.41526 | 0.00089882 | 37072.5865 | 0.023697 | 1.6945 | 27.8133 | 32.36 | 2.175 | 0.19616
2025-02-06 02:25 | 0.37913 | 0.4304 | 26.3841 | 0.041648 | 0.97878 | 0.41653 | 0.00090158 | 37186.1911 | 0.023697 | 1.6945 | 27.8865 | 32.4452 | 2.1888 | 0.1974
2025-02-06 02:26 | 0.37488 | 0.42557 | 26.3841 | 0.041648 | 0.97878 | 0.41186 | 0.00089148 | 36769.6446 | 0.023697 | 1.6945 | 27.6177 | 32.1324 | 2.1655 | 0.1953
2025-02-06 02:27 | 0.35751 | 0.40585 | 26.3841 | 0.041624 | 0.97878 | 0.39278 | 0.00085016 | 35065.5926 | 0.023697 | 1.6945 | 26.5133 | 30.8475 | 2.0689 | 0.18659
2025-02-06 02:28 | 0.35404 | 0.40191 | 26.3841 | 0.041745 | 0.97878 | 0.38896 | 0.0008419 | 34724.7814 | 0.023697 | 1.6945 | 26.2916 | 30.5895 | 2.0557 | 0.1854
2025-02-06 02:29 | 0.36832 | 0.41812 | 26.3841 | 0.041912 | 0.97878 | 0.40465 | 0.00087587 | 36125.8909 | 0.023697 | 1.6945 | 27.2013 | 31.648 | 2.143 | 0.19327
2025-02-06 02:30 | 0.37875 | 0.42996 | 26.3839 | 0.041907 | 0.97878 | 0.4161 | 0.00090066 | 37148.2774 | 0.023697 | 1.6945 | 27.8621 | 32.4166 | 2.2003 | 0.19844
2025-02-06 02:31 | 0.37064 | 0.42075 | 26.3833 | 0.041838 | 0.97878 | 0.4072 | 0.00088138 | 36352.929 | 0.023698 | 1.6945 | 27.3484 | 31.8185 | 2.152 | 0.19408
2025-02-06 02:32 | 0.36292 | 0.41198 | 26.3826 | 0.041764 | 0.97878 | 0.39871 | 0.00086302 | 35595.4521 | 0.023698 | 1.6945 | 26.8577 | 31.2471 | 2.1056 | 0.1899
2025-02-06 02:33 | 0.33087 | 0.37561 | 26.382 | 0.041745 | 0.97878 | 0.36351 | 0.00078681 | 32452.3362 | 0.023698 | 1.6944 | 24.8052 | 28.8587 | 1.9275 | 0.17383
2025-02-06 02:34 | 0.30693 | 0.34843 | 26.3813 | 0.041717 | 0.97878 | 0.33721 | 0.00072989 | 30104.455 | 0.023699 | 1.6944 | 23.2538 | 27.0534 | 1.7933 | 0.16174
2025-02-06 02:35 | 0.33049 | 0.37517 | 26.3808 | 0.041598 | 0.97878 | 0.36308 | 0.0007859 | 32414.2641 | 0.023699 | 1.6944 | 24.7803 | 28.8289 | 1.9185 | 0.17303
2025-02-06 02:36 | 0.32894 | 0.37341 | 26.3805 | 0.041602 | 0.97878 | 0.36139 | 0.00078222 | 32262.7408 | 0.023699 | 1.6944 | 24.6807 | 28.7128 | 1.9101 | 0.17227
2025-02-06 02:37 | 0.3274 | 0.37166 | 26.3802 | 0.041598 | 0.97878 | 0.35969 | 0.00077855 | 32111.2196 | 0.0237 | 1.6944 | 24.581 | 28.5966 | 1.9014 | 0.17149
2025-02-06 02:38 | 0.3745 | 0.42513 | 26.3799 | 0.041626 | 0.97879 | 0.41144 | 0.00089056 | 36730.9325 | 0.0237 | 1.6944 | 27.5932 | 32.1007 | 2.162 | 0.19499
2025-02-06 02:39 | 0.37797 | 0.42907 | 26.3796 | 0.04172 | 0.97879 | 0.41526 | 0.00089882 | 37071.674 | 0.0237 | 1.6943 | 27.8133 | 32.3565 | 2.186 | 0.19715
2025-02-06 02:40 | 0.36755 | 0.41724 | 26.3793 | 0.041694 | 0.97879 | 0.4038 | 0.00087403 | 36049.2089 | 0.0237 | 1.6943 | 27.1523 | 31.5873 | 2.1273 | 0.19186
2025-02-06 02:41 | 0.36253 | 0.41154 | 26.379 | 0.041574 | 0.97879 | 0.39829 | 0.0008621 | 35556.8801 | 0.023701 | 1.6943 | 26.8331 | 31.2158 | 2.0936 | 0.18882
2025-02-06 02:42 | 0.3745 | 0.42512 | 26.3785 | 0.041505 | 0.97879 | 0.41144 | 0.00089056 | 36730.6652 | 0.023701 | 1.6943 | 27.5932 | 32.0997 | 2.1556 | 0.19441
2025-02-06 02:43 | 0.38183 | 0.43345 | 26.3779 | 0.041578 | 0.97879 | 0.4195 | 0.000908 | 37450.002 | 0.023701 | 1.6943 | 28.0574 | 32.6392 | 2.1996 | 0.19838
2025-02-06 02:44 | 0.39419 | 0.44747 | 26.3772 | 0.041672 | 0.97879 | 0.43307 | 0.00093738 | 38661.5969 | 0.023702 | 1.6942 | 28.8364 | 33.5449 | 2.2722 | 0.20492
2025-02-06 02:45 | 0.39033 | 0.44309 | 26.3766 | 0.041621 | 0.97879 | 0.42883 | 0.0009282 | 38282.7988 | 0.023702 | 1.6942 | 28.5933 | 33.2616 | 2.2483 | 0.20277
2025-02-06 02:46 | 0.34863 | 0.39575 | 26.3759 | 0.041454 | 0.97879 | 0.38302 | 0.00082905 | 34193.1217 | 0.023703 | 1.6942 | 25.946 | 30.1816 | 2.0113 | 0.18139
2025-02-06 02:47 | 0.33203 | 0.37691 | 26.3755 | 0.041312 | 0.97879 | 0.36478 | 0.00078957 | 32564.8049 | 0.023703 | 1.6942 | 24.8798 | 28.9411 | 1.9135 | 0.17257
2025-02-06 02:48 | 0.35056 | 0.39794 | 26.3755 | 0.041492 | 0.97879 | 0.38514 | 0.00083364 | 34382.3745 | 0.023703 | 1.6942 | 26.0695 | 30.325 | 2.0237 | 0.18251
2025-02-06 02:49 | 0.35365 | 0.40145 | 26.3755 | 0.041466 | 0.97879 | 0.38853 | 0.00084098 | 34685.303 | 0.023703 | 1.6942 | 26.2669 | 30.5546 | 2.0394 | 0.18393
2025-02-06 02:50 | 0.33898 | 0.3848 | 26.3755 | 0.041266 | 0.97879 | 0.37242 | 0.00080609 | 33246.3923 | 0.023703 | 1.6942 | 25.327 | 29.4613 | 1.9494 | 0.17581
2025-02-06 02:51 | 0.32585 | 0.3699 | 26.3755 | 0.041342 | 0.97879 | 0.35799 | 0.00077488 | 31958.9465 | 0.023703 | 1.6942 | 24.4812 | 28.4774 | 1.881 | 0.16964
2025-02-06 02:52 | 0.32083 | 0.3642 | 26.3755 | 0.041511 | 0.97879 | 0.35248 | 0.00076294 | 31466.6883 | 0.023703 | 1.6942 | 24.1566 | 28.0998 | 1.861 | 0.16784
2025-02-06 02:53 | 0.33859 | 0.38436 | 26.3755 | 0.041473 | 0.97879 | 0.37199 | 0.00080518 | 33208.5259 | 0.023703 | 1.6942 | 25.3022 | 29.4324 | 1.957 | 0.1765
2025-02-06 02:54 | 0.35983 | 0.40846 | 26.3755 | 0.041438 | 0.97879 | 0.39532 | 0.00085567 | 35291.1441 | 0.023703 | 1.6942 | 26.661 | 31.013 | 2.0718 | 0.18685
2025-02-06 02:55 | 0.37836 | 0.4295 | 26.3752 | 0.04153 | 0.97879 | 0.41568 | 0.00089974 | 37108.6707 | 0.023703 | 1.6941 | 27.8377 | 32.3816 | 2.1779 | 0.19642
2025-02-06 02:56 | 0.38338 | 0.4352 | 26.375 | 0.041425 | 0.9788 | 0.42119 | 0.00091168 | 37600.8854 | 0.023703 | 1.6941 | 28.155 | 32.7505 | 2.1997 | 0.19839
2025-02-06 02:57 | 0.37141 | 0.42161 | 26.3748 | 0.041263 | 0.9788 | 0.40805 | 0.00088321 | 36427.0002 | 0.023703 | 1.6941 | 27.3974 | 31.8691 | 2.126 | 0.19174
2025-02-06 02:58 | 0.35828 | 0.40671 | 26.3746 | 0.041168 | 0.9788 | 0.39362 | 0.000852 | 35139.5178 | 0.023704 | 1.6941 | 26.5626 | 30.8978 | 2.0498 | 0.18487
2025-02-06 02:59 | 0.35133 | 0.39882 | 26.3741 | 0.041199 | 0.9788 | 0.38599 | 0.00083547 | 34457.8339 | 0.023704 | 1.6941 | 26.1189 | 30.3813 | 2.0135 | 0.1816
2025-02-06 03:00 | 0.35481 | 0.40276 | 26.373 | 0.041317 | 0.9788 | 0.38981 | 0.00084374 | 34798.4249 | 0.023705 | 1.694 | 26.3409 | 30.6388 | 2.0382 | 0.18382
2025-02-06 03:01 | 0.34438 | 0.39092 | 26.3719 | 0.041311 | 0.9788 | 0.37835 | 0.00081895 | 33775.8594 | 0.023706 | 1.694 | 25.6739 | 29.8623 | 1.9809 | 0.17865
2025-02-06 03:02 | 0.32392 | 0.36769 | 26.3709 | 0.041419 | 0.9788 | 0.35587 | 0.00077029 | 31768.813 | 0.023706 | 1.6939 | 24.3565 | 28.3292 | 1.8736 | 0.16898
2025-02-06 03:03 | 0.33357 | 0.37865 | 26.3698 | 0.041476 | 0.97881 | 0.36648 | 0.00079324 | 32715.2508 | 0.023707 | 1.6939 | 24.9793 | 29.0529 | 1.9293 | 0.174
2025-02-06 03:04 | 0.36021 | 0.40889 | 26.3689 | 0.041409 | 0.97881 | 0.39574 | 0.00085659 | 35327.7518 | 0.023708 | 1.6939 | 26.6856 | 31.0367 | 2.0721 | 0.18687
2025-02-06 03:05 | 0.36948 | 0.4194 | 26.3682 | 0.041409 | 0.97881 | 0.40592 | 0.00087862 | 36236.3764 | 0.023708 | 1.6938 | 27.2749 | 31.7216 | 2.1226 | 0.19144
2025-02-06 03:06 | 0.38608 | 0.43825 | 26.3676 | 0.04146 | 0.97881 | 0.42416 | 0.0009181 | 37864.4207 | 0.023709 | 1.6938 | 28.3256 | 32.9431 | 2.2158 | 0.19984
2025-02-06 03:07 | 0.37141 | 0.42159 | 26.3669 | 0.041403 | 0.97881 | 0.40805 | 0.00088321 | 36425.4459 | 0.023709 | 1.6938 | 27.3974 | 31.8631 | 2.1328 | 0.19235
2025-02-06 03:08 | 0.38338 | 0.43517 | 26.3663 | 0.041391 | 0.97881 | 0.42119 | 0.00091168 | 37599.1069 | 0.02371 | 1.6937 | 28.155 | 32.7437 | 2.1974 | 0.19817
2025-02-06 03:09 | 0.38454 | 0.43649 | 26.3655 | 0.041509 | 0.97881 | 0.42247 | 0.00091443 | 37712.5349 | 0.02371 | 1.6937 | 28.2281 | 32.8281 | 2.2099 | 0.1993
2025-02-06 03:10 | 0.32508 | 0.369 | 26.3644 | 0.041474 | 0.97882 | 0.35715 | 0.00077304 | 31881.2957 | 0.023711 | 1.6937 | 24.4313 | 28.4119 | 1.8821 | 0.16974
2025-02-06 03:11 | 0.32392 | 0.36768 | 26.3633 | 0.041331 | 0.97882 | 0.35587 | 0.00077029 | 31767.5216 | 0.023712 | 1.6936 | 24.3565 | 28.3241 | 1.8692 | 0.16858
2025-02-06 03:12 | 0.3772 | 0.42815 | 26.3623 | 0.041319 | 0.97882 | 0.41441 | 0.00089699 | 36992.4786 | 0.023712 | 1.6936 | 27.7644 | 32.2864 | 2.1597 | 0.19477
2025-02-06 03:13 | 0.37218 | 0.42245 | 26.3612 | 0.041152 | 0.97882 | 0.40889 | 0.00088505 | 36500.0435 | 0.023713 | 1.6935 | 27.4464 | 31.9158 | 2.1237 | 0.19153
2025-02-06 03:14 | 0.35944 | 0.40799 | 26.3601 | 0.041137 | 0.97883 | 0.3949 | 0.00085475 | 35250.3572 | 0.023714 | 1.6935 | 26.6364 | 30.9731 | 2.0537 | 0.18522
2025-02-06 03:15 | 0.34516 | 0.39177 | 26.3591 | 0.041141 | 0.97883 | 0.3792 | 0.00082078 | 33849.2336 | 0.023715 | 1.6934 | 25.7234 | 29.9107 | 1.9762 | 0.17823
2025-02-06 03:16 | 0.33666 | 0.38213 | 26.3583 | 0.040906 | 0.97883 | 0.36987 | 0.00080059 | 33016.1172 | 0.023715 | 1.6934 | 25.1781 | 29.2761 | 1.9189 | 0.17306
2025-02-06 03:17 | 0.3745 | 0.42508 | 26.3581 | 0.040814 | 0.97883 | 0.41144 | 0.00089056 | 36726.5987 | 0.023715 | 1.6934 | 27.5932 | 32.0841 | 2.1185 | 0.19106
2025-02-06 03:18 | 0.41813 | 0.4746 | 26.3579 | 0.040936 | 0.97883 | 0.45937 | 0.00099431 | 41005.01 | 0.023715 | 1.6934 | 30.3361 | 35.2732 | 2.3592 | 0.21277
2025-02-06 03:19 | 0.41272 | 0.46846 | 26.3576 | 0.041102 | 0.97883 | 0.45343 | 0.00098145 | 40474.8899 | 0.023716 | 1.6934 | 29.9985 | 34.8805 | 2.3397 | 0.21101
2025-02-06 03:20 | 0.38029 | 0.43165 | 26.3574 | 0.041195 | 0.97883 | 0.4178 | 0.00090433 | 37294.4071 | 0.023716 | 1.6933 | 27.9598 | 32.5099 | 2.1697 | 0.19568
2025-02-06 03:21 | 0.38647 | 0.43866 | 26.3577 | 0.041218 | 0.97883 | 0.42459 | 0.00091902 | 37900.2531 | 0.023716 | 1.6934 | 28.3499 | 32.9637 | 2.2044 | 0.19881
2025-02-06 03:22 | 0.42353 | 0.48073 | 26.3587 | 0.041268 | 0.97883 | 0.46531 | 0.0010072 | 41535.2791 | 0.023715 | 1.6934 | 30.673 | 35.6657 | 2.4076 | 0.21713
2025-02-06 03:23 | 0.41079 | 0.46627 | 26.3598 | 0.041363 | 0.97883 | 0.45131 | 0.00097686 | 40286.0451 | 0.023714 | 1.6934 | 29.8778 | 34.7419 | 2.3442 | 0.21142
2025-02-06 03:24 | 0.39689 | 0.4505 | 26.3609 | 0.041434 | 0.97882 | 0.43604 | 0.00094381 | 38923.2099 | 0.023713 | 1.6935 | 29.0063 | 33.7295 | 2.2728 | 0.20498
2025-02-06 03:25 | 0.40963 | 0.46496 | 26.3619 | 0.041284 | 0.97882 | 0.45004 | 0.00097411 | 40172.9241 | 0.023713 | 1.6935 | 29.8053 | 34.6594 | 2.3337 | 0.21047
2025-02-06 03:26 | 0.42199 | 0.47899 | 26.3624 | 0.041197 | 0.97882 | 0.46361 | 0.0010035 | 41384.6537 | 0.023712 | 1.6936 | 30.5768 | 35.557 | 2.3954 | 0.21603
2025-02-06 03:27 | 0.44515 | 0.50528 | 26.3618 | 0.041266 | 0.97882 | 0.48906 | 0.0010586 | 43656.3085 | 0.023713 | 1.6935 | 32.0149 | 37.2287 | 2.5242 | 0.22765
2025-02-06 03:28 | 0.43164 | 0.48994 | 26.3611 | 0.041192 | 0.97882 | 0.47421 | 0.0010264 | 42330.9481 | 0.023713 | 1.6935 | 31.1773 | 36.2542 | 2.447 | 0.22069
2025-02-06 03:29 | 0.37836 | 0.42946 | 26.3605 | 0.041049 | 0.97882 | 0.41568 | 0.00089974 | 37105.7108 | 0.023714 | 1.6935 | 27.8377 | 32.3703 | 2.1517 | 0.19406
2025-02-06 03:30 | 0.37218 | 0.42245 | 26.3599 | 0.041103 | 0.97883 | 0.40889 | 0.00088505 | 36499.7756 | 0.023714 | 1.6935 | 27.4464 | 31.9147 | 2.1211 | 0.1913
2025-02-06 03:31 | 0.39187 | 0.4448 | 26.3594 | 0.041021 | 0.97883 | 0.43053 | 0.00093187 | 38430.6943 | 0.023714 | 1.6934 | 28.6906 | 33.3612 | 2.2231 | 0.20049
2025-02-06 03:32 | 0.40461 | 0.45926 | 26.3594 | 0.040911 | 0.97883 | 0.44452 | 0.00096217 | 39680.163 | 0.023714 | 1.6934 | 29.491 | 34.2919 | 2.2855 | 0.20612
2025-02-06 03:33 | 0.42816 | 0.48599 | 26.3594 | 0.04093 | 0.97883 | 0.4704 | 0.0010182 | 41989.7921 | 0.023714 | 1.6934 | 30.9613 | 36.0016 | 2.4127 | 0.21759
2025-02-06 03:34 | 0.42894 | 0.48687 | 26.3594 | 0.040986 | 0.97883 | 0.47125 | 0.00102 | 42065.5179 | 0.023714 | 1.6934 | 31.0094 | 36.0574 | 2.4202 | 0.21827
2025-02-06 03:35 | 0.39921 | 0.45313 | 26.3594 | 0.041025 | 0.97883 | 0.43858 | 0.00094932 | 39150.0857 | 0.023714 | 1.6934 | 29.1519 | 33.8976 | 2.2627 | 0.20407
2025-02-06 03:36 | 0.36137 | 0.41018 | 26.3594 | 0.041005 | 0.97883 | 0.39702 | 0.00085934 | 35439.537 | 0.023714 | 1.6934 | 26.7594 | 31.1156 | 2.0576 | 0.18557
2025-02-06 03:37 | 0.34786 | 0.39484 | 26.3594 | 0.041002 | 0.97883 | 0.38217 | 0.00082721 | 34114.3401 | 0.023714 | 1.6934 | 25.8966 | 30.1123 | 1.9842 | 0.17895
2025-02-06 03:38 | 0.32701 | 0.37118 | 26.3593 | 0.040904 | 0.97883 | 0.35927 | 0.00077763 | 32069.724 | 0.023714 | 1.6934 | 24.556 | 28.5535 | 1.8665 | 0.16833
2025-02-06 03:39 | 0.3301 | 0.37468 | 26.3589 | 0.040735 | 0.97883 | 0.36266 | 0.00078498 | 32372.5521 | 0.023715 | 1.6934 | 24.7554 | 28.785 | 1.8754 | 0.16914
2025-02-06 03:40 | 0.33821 | 0.38388 | 26.3584 | 0.041002 | 0.97883 | 0.37157 | 0.00080426 | 33167.5908 | 0.023715 | 1.6934 | 25.2774 | 29.3916 | 1.9318 | 0.17422
2025-02-06 03:41 | 0.34979 | 0.39703 | 26.358 | 0.041136 | 0.97883 | 0.38429 | 0.0008318 | 34303.3873 | 0.023715 | 1.6934 | 26.0201 | 30.2549 | 2.0011 | 0.18047
2025-02-06 03:42 | 0.38531 | 0.43735 | 26.3576 | 0.040955 | 0.97883 | 0.42332 | 0.00091627 | 37786.6445 | 0.023716 | 1.6933 | 28.2768 | 32.8786 | 2.184 | 0.19697
2025-02-06 03:43 | 0.38145 | 0.43296 | 26.3574 | 0.040958 | 0.97883 | 0.41907 | 0.00090709 | 37407.9876 | 0.023716 | 1.6933 | 28.033 | 32.595 | 2.1634 | 0.19511
2025-02-06 03:44 | 0.36523 | 0.41456 | 26.3577 | 0.041082 | 0.97883 | 0.40126 | 0.00086853 | 35817.8281 | 0.023716 | 1.6934 | 27.0051 | 31.4 | 2.0822 | 0.18779
2025-02-06 03:45 | 0.39728 | 0.45093 | 26.358 | 0.041272 | 0.97883 | 0.43646 | 0.00094473 | 38960.4703 | 0.023715 | 1.6934 | 29.0306 | 33.7554 | 2.2659 | 0.20435
2025-02-06 03:46 | 0.38145 | 0.43296 | 26.3583 | 0.041362 | 0.97883 | 0.41907 | 0.00090709 | 37408.1717 | 0.023715 | 1.6934 | 28.033 | 32.5957 | 2.1848 | 0.19704
2025-02-06 03:47 | 0.3745 | 0.42508 | 26.3586 | 0.041438 | 0.97883 | 0.41144 | 0.00089056 | 36726.7079 | 0.023715 | 1.6934 | 27.5932 | 32.0846 | 2.1509 | 0.19399
2025-02-06 03:48 | 0.34709 | 0.39396 | 26.3589 | 0.041428 | 0.97883 | 0.38132 | 0.00082537 | 34038.5206 | 0.023715 | 1.6934 | 25.8471 | 30.0544 | 2.0006 | 0.18043
2025-02-06 03:49 | 0.32817 | 0.37249 | 26.3592 | 0.041387 | 0.97883 | 0.36054 | 0.00078039 | 32183.3049 | 0.023714 | 1.6934 | 24.6308 | 28.6404 | 1.8949 | 0.17089
2025-02-06 03:50 | 0.35635 | 0.40448 | 26.3594 | 0.041409 | 0.97883 | 0.3915 | 0.00084741 | 34947.3201 | 0.023714 | 1.6934 | 26.4394 | 30.7436 | 2.0504 | 0.18492
2025-02-06 03:51 | 0.36407 | 0.41325 | 26.3594 | 0.041307 | 0.97883 | 0.39999 | 0.00086577 | 35704.5757 | 0.023714 | 1.6934 | 26.9314 | 31.3156 | 2.0874 | 0.18826
2025-02-06 03:52 | 0.3938 | 0.44699 | 26.3594 | 0.041322 | 0.97883 | 0.43265 | 0.00093646 | 38620.0073 | 0.023714 | 1.6934 | 28.8121 | 33.5025 | 2.2498 | 0.20291
2025-02-06 03:53 | 0.3745 | 0.42508 | 26.3594 | 0.041252 | 0.97883 | 0.41144 | 0.00089056 | 36726.8697 | 0.023714 | 1.6934 | 27.5932 | 32.0852 | 2.1413 | 0.19312
2025-02-06 03:54 | 0.32817 | 0.37249 | 26.3594 | 0.041228 | 0.97883 | 0.36054 | 0.00078039 | 32183.3394 | 0.023714 | 1.6934 | 24.6308 | 28.6405 | 1.8876 | 0.17024
2025-02-06 03:55 | 0.27991 | 0.31771 | 26.3594 | 0.041209 | 0.97883 | 0.30752 | 0.00066562 | 27450.4956 | 0.023714 | 1.6934 | 21.4817 | 24.9788 | 1.6216 | 0.14625
2025-02-06 03:56 | 0.28686 | 0.3256 | 26.3594 | 0.04128 | 0.97883 | 0.31515 | 0.00068215 | 28132.0256 | 0.023714 | 1.6934 | 21.9396 | 25.5112 | 1.6628 | 0.14997
2025-02-06 03:57 | 0.34786 | 0.39484 | 26.3593 | 0.041252 | 0.97883 | 0.38217 | 0.00082721 | 34114.311 | 0.023714 | 1.6934 | 25.8966 | 30.1122 | 1.9963 | 0.18004
2025-02-06 03:58 | 0.33435 | 0.3795 | 26.3588 | 0.041097 | 0.97883 | 0.36733 | 0.00079508 | 32789.0401 | 0.023715 | 1.6934 | 25.029 | 29.1032 | 1.9152 | 0.17273
2025-02-06 03:59 | 0.32547 | 0.36942 | 26.3584 | 0.040944 | 0.97883 | 0.35757 | 0.00077396 | 31918.1252 | 0.023715 | 1.6934 | 24.4563 | 28.4369 | 1.8599 | 0.16774
2025-02-06 04:00 | 0.35635 | 0.40448 | 26.358 | 0.040863 | 0.97883 | 0.3915 | 0.00084741 | 34947.0475 | 0.023715 | 1.6934 | 26.4394 | 30.7425 | 2.0233 | 0.18247
2025-02-06 04:01 | 0.32354 | 0.36723 | 26.3576 | 0.040885 | 0.97883 | 0.35545 | 0.00076937 | 31728.665 | 0.023716 | 1.6933 | 24.3315 | 28.2912 | 1.8466 | 0.16654
2025-02-06 04:02 | 0.31968 | 0.36285 | 26.3575 | 0.040937 | 0.97883 | 0.35121 | 0.00076019 | 31350.0364 | 0.023716 | 1.6933 | 24.0816 | 28.0006 | 1.828 | 0.16486
2025-02-06 04:03 | 0.34245 | 0.3887 | 26.3582 | 0.04098 | 0.97883 | 0.37623 | 0.00081436 | 33584.0307 | 0.023715 | 1.6934 | 25.5501 | 29.7086 | 1.9538 | 0.1762
2025-02-06 04:04 | 0.31736 | 0.36022 | 26.3588 | 0.040954 | 0.97883 | 0.34866 | 0.00075468 | 31123.0772 | 0.023715 | 1.6934 | 23.9314 | 27.8268 | 1.8162 | 0.1638
2025-02-06 04:05 | 0.30307 | 0.34401 | 26.3595 | 0.041011 | 0.97883 | 0.33297 | 0.00072071 | 29722.2637 | 0.023714 | 1.6934 | 23.0021 | 26.7466 | 1.7408 | 0.157
2025-02-06 04:06 | 0.30385 | 0.34489 | 26.3601 | 0.040918 | 0.97883 | 0.33382 | 0.00072255 | 29798.0929 | 0.023714 | 1.6935 | 23.0524 | 26.8056 | 1.7411 | 0.15702
2025-02-06 04:07 | 0.28956 | 0.32867 | 26.3603 | 0.040789 | 0.97883 | 0.31812 | 0.00068858 | 28397.2035 | 0.023714 | 1.6935 | 22.1173 | 25.7183 | 1.6578 | 0.14952
2025-02-06 04:08 | 0.3023 | 0.34313 | 26.3599 | 0.040868 | 0.97883 | 0.33212 | 0.00071887 | 29646.613 | 0.023714 | 1.6935 | 22.9516 | 26.6883 | 1.7305 | 0.15607
2025-02-06 04:09 | 0.34091 | 0.38695 | 26.3595 | 0.040959 | 0.97883 | 0.37454 | 0.00081068 | 33432.8204 | 0.023714 | 1.6934 | 25.451 | 29.5943 | 1.9444 | 0.17536
2025-02-06 04:10 | 0.344 | 0.39046 | 26.3591 | 0.041006 | 0.97883 | 0.37793 | 0.00081803 | 33735.6436 | 0.023715 | 1.6934 | 25.6492 | 29.8244 | 1.9634 | 0.17708
2025-02-06 04:11 | 0.35018 | 0.39747 | 26.3586 | 0.041001 | 0.97883 | 0.38472 | 0.00083272 | 34341.3658 | 0.023715 | 1.6934 | 26.0448 | 30.2841 | 1.9967 | 0.18008
2025-02-06 04:12 | 0.32817 | 0.37249 | 26.3584 | 0.04106 | 0.97883 | 0.36054 | 0.00078039 | 32183.1528 | 0.023715 | 1.6934 | 24.6308 | 28.6398 | 1.8798 | 0.16954
2025-02-06 04:13 | 0.3108 | 0.35277 | 26.3584 | 0.04115 | 0.97883 | 0.34145 | 0.00073907 | 30479.3384 | 0.023715 | 1.6934 | 23.5052 | 27.3309 | 1.789 | 0.16134
2025-02-06 04:14 | 0.32238 | 0.36592 | 26.3584 | 0.041117 | 0.97883 | 0.35418 | 0.00076662 | 31615.2146 | 0.023715 | 1.6934 | 24.2566 | 28.2046 | 1.8508 | 0.16692
2025-02-06 04:15 | 0.32161 | 0.36504 | 26.3584 | 0.041102 | 0.97883 | 0.35333 | 0.00076478 | 31539.4896 | 0.023715 | 1.6934 | 24.2066 | 28.1465 | 1.846 | 0.16648
2025-02-06 04:16 | 0.31852 | 0.36153 | 26.3584 | 0.041069 | 0.97883 | 0.34993 | 0.00075743 | 31236.5887 | 0.023715 | 1.6934 | 24.0065 | 27.9139 | 1.8276 | 0.16483
2025-02-06 04:17 | 0.32778 | 0.37205 | 26.3584 | 0.041055 | 0.97883 | 0.36011 | 0.00077947 | 32145.2892 | 0.023715 | 1.6934 | 24.6059 | 28.6108 | 1.8775 | 0.16933
2025-02-06 04:18 | 0.3135 | 0.35584 | 26.3584 | 0.041021 | 0.97883 | 0.34442 | 0.0007455 | 30744.3757 | 0.023715 | 1.6934 | 23.6808 | 27.5352 | 1.7981 | 0.16217
2025-02-06 04:19 | 0.28068 | 0.31859 | 26.3579 | 0.04098 | 0.97883 | 0.30837 | 0.00066746 | 27525.9982 | 0.023715 | 1.6934 | 21.5327 | 25.0371 | 1.6168 | 0.14582
2025-02-06 04:20 | 0.30076 | 0.34137 | 26.3569 | 0.041061 | 0.97883 | 0.33042 | 0.0007152 | 29494.6749 | 0.023716 | 1.6933 | 22.8508 | 26.5691 | 1.7301 | 0.15603
2025-02-06 04:21 | 0.29883 | 0.33918 | 26.3558 | 0.041204 | 0.97883 | 0.3283 | 0.00071061 | 29305.1943 | 0.023717 | 1.6933 | 22.7246 | 26.4217 | 1.7255 | 0.15562
2025-02-06 04:22 | 0.30539 | 0.34663 | 26.3547 | 0.041104 | 0.97884 | 0.33551 | 0.00072622 | 29948.6756 | 0.023718 | 1.6932 | 23.1532 | 26.9193 | 1.7572 | 0.15848
2025-02-06 04:23 | 0.29767 | 0.33786 | 26.3537 | 0.04098 | 0.97884 | 0.32703 | 0.00070786 | 29191.2699 | 0.023718 | 1.6932 | 22.6488 | 26.3322 | 1.7096 | 0.15419
2025-02-06 04:24 | 0.30578 | 0.34706 | 26.3531 | 0.040926 | 0.97884 | 0.33594 | 0.00072714 | 29986.2692 | 0.023719 | 1.6931 | 23.1783 | 26.9475 | 1.7516 | 0.15797
2025-02-06 04:25 | 0.30385 | 0.34487 | 26.3533 | 0.040966 | 0.97884 | 0.33382 | 0.00072255 | 29796.9955 | 0.023719 | 1.6932 | 23.0524 | 26.8013 | 1.7428 | 0.15718
2025-02-06 04:26 | 0.31466 | 0.35714 | 26.3535 | 0.041055 | 0.97884 | 0.34569 | 0.00074825 | 30857.1531 | 0.023719 | 1.6932 | 23.7561 | 27.6195 | 1.8056 | 0.16285
2025-02-06 04:27 | 0.3162 | 0.3589 | 26.3537 | 0.041075 | 0.97884 | 0.34739 | 0.00075193 | 31008.6354 | 0.023718 | 1.6932 | 23.8563 | 27.7361 | 1.815 | 0.16369
2025-02-06 04:28 | 0.28416 | 0.32252 | 26.3539 | 0.041102 | 0.97884 | 0.31218 | 0.00067572 | 27866.1573 | 0.023718 | 1.6932 | 21.7617 | 25.3011 | 1.6406 | 0.14796
2025-02-06 04:29 | 0.29458 | 0.33436 | 26.3538 | 0.04115 | 0.97884 | 0.32364 | 0.00070051 | 28888.4038 | 0.023718 | 1.6932 | 22.4466 | 26.0972 | 1.6998 | 0.1533
2025-02-06 04:30 | 0.29921 | 0.33961 | 26.3532 | 0.041063 | 0.97884 | 0.32873 | 0.00071153 | 29342.6456 | 0.023719 | 1.6932 | 22.7498 | 26.4494 | 1.7215 | 0.15526
2025-02-06 04:31 | 0.30076 | 0.34137 | 26.3526 | 0.041035 | 0.97884 | 0.33042 | 0.0007152 | 29493.9931 | 0.023719 | 1.6931 | 22.8508 | 26.5664 | 1.7288 | 0.15591
2025-02-06 04:32 | 0.30192 | 0.34268 | 26.352 | 0.041103 | 0.97884 | 0.3317 | 0.00071796 | 29607.4792 | 0.02372 | 1.6931 | 22.9264 | 26.654 | 1.738 | 0.15674
2025-02-06 04:33 | 0.25481 | 0.28922 | 26.3514 | 0.04104 | 0.97884 | 0.27995 | 0.00060595 | 24988.3263 | 0.02372 | 1.6931 | 19.8147 | 23.0359 | 1.4764 | 0.13315
2025-02-06 04:34 | 0.2969 | 0.33698 | 26.3508 | 0.040897 | 0.97884 | 0.32618 | 0.00070602 | 29115.0889 | 0.02372 | 1.693 | 22.5983 | 26.2717 | 1.7018 | 0.15348
2025-02-06 04:35 | 0.28531 | 0.32383 | 26.3501 | 0.040837 | 0.97885 | 0.31346 | 0.00067848 | 27979.1672 | 0.023721 | 1.693 | 21.838 | 25.3875 | 1.6361 | 0.14756
2025-02-06 04:36 | 0.27335 | 0.31025 | 26.3497 | 0.040865 | 0.97885 | 0.30031 | 0.00065002 | 26805.4155 | 0.023721 | 1.693 | 21.0478 | 24.4686 | 1.5717 | 0.14175
2025-02-06 04:37 | 0.31157 | 0.35363 | 26.3495 | 0.040885 | 0.97885 | 0.3423 | 0.00074091 | 30553.5946 | 0.023721 | 1.693 | 23.5554 | 27.3835 | 1.7812 | 0.16064
2025-02-06 04:38 | 0.33319 | 0.37817 | 26.3493 | 0.040857 | 0.97885 | 0.36605 | 0.00079232 | 32673.7567 | 0.023722 | 1.693 | 24.9545 | 29.0098 | 1.8972 | 0.17111
2025-02-06 04:39 | 0.3135 | 0.35582 | 26.3491 | 0.040837 | 0.97885 | 0.34442 | 0.0007455 | 30742.8265 | 0.023722 | 1.693 | 23.6808 | 27.5291 | 1.7895 | 0.16139
2025-02-06 04:40 | 0.29419 | 0.33391 | 26.3488 | 0.041087 | 0.97885 | 0.32321 | 0.00069959 | 28849.7622 | 0.023722 | 1.693 | 22.4213 | 26.0647 | 1.6948 | 0.15285
2025-02-06 04:41 | 0.32161 | 0.36502 | 26.3484 | 0.041099 | 0.97885 | 0.35333 | 0.00076478 | 31537.7979 | 0.023722 | 1.6929 | 24.2066 | 28.1399 | 1.8453 | 0.16642
2025-02-06 04:42 | 0.30153 | 0.34223 | 26.3478 | 0.04073 | 0.97885 | 0.33127 | 0.00071704 | 29568.9493 | 0.023723 | 1.6929 | 22.9012 | 26.622 | 1.7199 | 0.15511
2025-02-06 04:43 | 0.30925 | 0.351 | 26.3472 | 0.040607 | 0.97885 | 0.33975 | 0.0007354 | 30326.0507 | 0.023723 | 1.6929 | 23.4047 | 27.2068 | 1.7564 | 0.15841
2025-02-06 04:44 | 0.27991 | 0.31769 | 26.3465 | 0.040646 | 0.97885 | 0.30752 | 0.00066562 | 27448.5767 | 0.023723 | 1.6929 | 21.4817 | 24.9711 | 1.5989 | 0.1442
2025-02-06 04:45 | 0.27914 | 0.31681 | 26.3459 | 0.040646 | 0.97885 | 0.30667 | 0.00066379 | 27372.7613 | 0.023724 | 1.6928 | 21.4308 | 24.9115 | 1.5947 | 0.14382
2025-02-06 04:46 | 0.31581 | 0.35844 | 26.3457 | 0.04073 | 0.97885 | 0.34697 | 0.00075101 | 30969.4374 | 0.023724 | 1.6928 | 23.8312 | 27.7018 | 1.7972 | 0.16209
2025-02-06 04:47 | 0.29111 | 0.3304 | 26.3464 | 0.040734 | 0.97885 | 0.31982 | 0.00069225 | 28546.4992 | 0.023724 | 1.6928 | 22.2187 | 25.8277 | 1.6633 | 0.15001
2025-02-06 04:48 | 0.26794 | 0.30411 | 26.347 | 0.040805 | 0.97885 | 0.29437 | 0.00063716 | 26274.9869 | 0.023723 | 1.6929 | 20.6894 | 24.0504 | 1.5397 | 0.13886
2025-02-06 04:49 | 0.29265 | 0.33215 | 26.3477 | 0.04066 | 0.97885 | 0.32152 | 0.00069592 | 28698.1415 | 0.023723 | 1.6929 | 22.32 | 25.9463 | 1.6687 | 0.1505
2025-02-06 04:50 | 0.31581 | 0.35845 | 26.3483 | 0.04056 | 0.97885 | 0.34697 | 0.00075101 | 30969.8699 | 0.023722 | 1.6929 | 23.8312 | 27.7035 | 1.7899 | 0.16142
2025-02-06 04:51 | 0.32006 | 0.36327 | 26.3485 | 0.04057 | 0.97885 | 0.35163 | 0.00076111 | 31386.368 | 0.023722 | 1.6929 | 24.1066 | 28.0237 | 1.8132 | 0.16353
2025-02-06 04:52 | 0.32971 | 0.37422 | 26.3481 | 0.040636 | 0.97885 | 0.36224 | 0.00078406 | 32332.8062 | 0.023722 | 1.6929 | 24.7305 | 28.7487 | 1.8682 | 0.16849
2025-02-06 04:53 | 0.29535 | 0.33522 | 26.3477 | 0.040609 | 0.97885 | 0.32448 | 0.00070235 | 28963.1613 | 0.023723 | 1.6929 | 22.4972 | 26.1522 | 1.6813 | 0.15163
2025-02-06 04:54 | 0.29921 | 0.3396 | 26.3472 | 0.040608 | 0.97885 | 0.32873 | 0.00071153 | 29341.6969 | 0.023723 | 1.6929 | 22.7498 | 26.4457 | 1.7022 | 0.15351
2025-02-06 04:55 | 0.34786 | 0.39481 | 26.3468 | 0.040646 | 0.97885 | 0.38217 | 0.00082721 | 34112.0096 | 0.023723 | 1.6929 | 25.8966 | 30.1033 | 1.9663 | 0.17733
2025-02-06 04:56 | 0.31929 | 0.36239 | 26.3468 | 0.040675 | 0.97885 | 0.35078 | 0.00075927 | 31310.3596 | 0.023723 | 1.6929 | 24.0566 | 27.9644 | 1.8136 | 0.16357
2025-02-06 04:57 | 0.29805 | 0.33829 | 26.3475 | 0.040694 | 0.97885 | 0.32745 | 0.00070878 | 29228.1519 | 0.023723 | 1.6929 | 22.6741 | 26.3577 | 1.6995 | 0.15327
2025-02-06 04:58 | 0.29883 | 0.33917 | 26.3481 | 0.040666 | 0.97885 | 0.3283 | 0.00071061 | 29303.975 | 0.023722 | 1.6929 | 22.7246 | 26.4169 | 1.7025 | 0.15355
2025-02-06 04:59 | 0.3189 | 0.36195 | 26.3488 | 0.040675 | 0.97885 | 0.35036 | 0.00075835 | 31272.8271 | 0.023722 | 1.693 | 24.0315 | 27.9366 | 1.8116 | 0.16339
2025-02-06 05:00 | 0.32238 | 0.3659 | 26.3494 | 0.040694 | 0.97885 | 0.35418 | 0.00076662 | 31613.6819 | 0.023721 | 1.693 | 24.2566 | 28.1986 | 1.8313 | 0.16516
2025-02-06 05:01 | 0.31581 | 0.35845 | 26.3495 | 0.040694 | 0.97885 | 0.34697 | 0.00075101 | 30970.0676 | 0.023721 | 1.693 | 23.8312 | 27.7042 | 1.7958 | 0.16196
2025-02-06 05:02 | 0.3355 | 0.3808 | 26.3489 | 0.040609 | 0.97885 | 0.3686 | 0.00079783 | 32900.8489 | 0.023722 | 1.693 | 25.1036 | 29.1829 | 1.8982 | 0.17119
2025-02-06 05:03 | 0.34554 | 0.39219 | 26.3482 | 0.040608 | 0.97885 | 0.37963 | 0.0008217 | 33885.1059 | 0.023722 | 1.6929 | 25.7482 | 29.9318 | 1.952 | 0.17605
2025-02-06 05:04 | 0.30655 | 0.34793 | 26.3476 | 0.040646 | 0.97885 | 0.33679 | 0.00072897 | 30061.0949 | 0.023723 | 1.6929 | 23.2287 | 27.0025 | 1.7435 | 0.15724
2025-02-06 05:05 | 0.32238 | 0.36589 | 26.3469 | 0.040589 | 0.97885 | 0.35418 | 0.00076662 | 31613.2579 | 0.023723 | 1.6929 | 24.2566 | 28.197 | 1.8265 | 0.16473
2025-02-06 05:06 | 0.34052 | 0.38649 | 26.3461 | 0.040554 | 0.97885 | 0.37411 | 0.00080977 | 33392.5366 | 0.023724 | 1.6928 | 25.4262 | 29.556 | 1.9224 | 0.17338
2025-02-06 05:07 | 0.32431 | 0.36808 | 26.345 | 0.040868 | 0.97886 | 0.3563 | 0.00077121 | 31802.2314 | 0.023725 | 1.6928 | 24.3814 | 28.3408 | 1.8494 | 0.16679
2025-02-06 05:08 | 0.30114 | 0.34179 | 26.344 | 0.040696 | 0.97886 | 0.33085 | 0.00071612 | 29530.4724 | 0.023725 | 1.6927 | 22.876 | 26.5903 | 1.7162 | 0.15478
2025-02-06 05:09 | 0.28802 | 0.32689 | 26.3429 | 0.040368 | 0.97886 | 0.31643 | 0.0006849 | 28243.0832 | 0.023726 | 1.6927 | 22.0158 | 25.5897 | 1.6316 | 0.14715
2025-02-06 05:10 | 0.30925 | 0.35099 | 26.3418 | 0.040342 | 0.97886 | 0.33975 | 0.0007354 | 30325.1716 | 0.023727 | 1.6926 | 23.4047 | 27.2034 | 1.7447 | 0.15735
2025-02-06 05:11 | 0.29535 | 0.33521 | 26.3418 | 0.040389 | 0.97886 | 0.32448 | 0.00070235 | 28962.2338 | 0.023727 | 1.6926 | 22.4972 | 26.1485 | 1.6719 | 0.15079
2025-02-06 05:12 | 0.27759 | 0.31506 | 26.343 | 0.040409 | 0.97886 | 0.30497 | 0.00066012 | 27220.9029 | 0.023726 | 1.6927 | 21.3288 | 24.7913 | 1.5769 | 0.14222
2025-02-06 05:13 | 0.26987 | 0.3063 | 26.3443 | 0.040552 | 0.97886 | 0.29649 | 0.00064175 | 26463.8998 | 0.023725 | 1.6928 | 20.8175 | 24.1978 | 1.5406 | 0.13894
2025-02-06 05:14 | 0.27991 | 0.31769 | 26.3456 | 0.040501 | 0.97886 | 0.30752 | 0.00066562 | 27448.4424 | 0.023724 | 1.6928 | 21.4817 | 24.9706 | 1.5932 | 0.14368
2025-02-06 05:15 | 0.29805 | 0.33829 | 26.3469 | 0.040468 | 0.97885 | 0.32745 | 0.00070878 | 29228.0624 | 0.023723 | 1.6929 | 22.6741 | 26.3574 | 1.69 | 0.15242
2025-02-06 05:16 | 0.32161 | 0.36502 | 26.3474 | 0.040706 | 0.97885 | 0.35333 | 0.00076478 | 31537.6267 | 0.023723 | 1.6929 | 24.2066 | 28.1392 | 1.8276 | 0.16483
2025-02-06 05:17 | 0.3108 | 0.35275 | 26.347 | 0.040747 | 0.97885 | 0.34145 | 0.00073907 | 30477.4678 | 0.023723 | 1.6929 | 23.5052 | 27.3236 | 1.7709 | 0.15971
2025-02-06 05:18 | 0.29381 | 0.33347 | 26.3466 | 0.040461 | 0.97885 | 0.32279 | 0.00069868 | 28811.5521 | 0.023723 | 1.6929 | 22.396 | 26.0339 | 1.6668 | 0.15032
2025-02-06 05:19 | 0.28686 | 0.32558 | 26.3462 | 0.040313 | 0.97885 | 0.31515 | 0.00068215 | 28130.0043 | 0.023724 | 1.6928 | 21.9396 | 25.5032 | 1.6232 | 0.1464
2025-02-06 05:20 | 0.28107 | 0.31901 | 26.3457 | 0.040345 | 0.97885 | 0.30879 | 0.00066838 | 27562.04 | 0.023724 | 1.6928 | 21.5582 | 25.0595 | 1.5933 | 0.14369
2025-02-06 05:21 | 0.28609 | 0.3247 | 26.3452 | 0.040734 | 0.97886 | 0.31431 | 0.00068031 | 28054.1398 | 0.023724 | 1.6928 | 21.8888 | 25.4436 | 1.636 | 0.14754
2025-02-06 05:22 | 0.27412 | 0.31112 | 26.3446 | 0.040428 | 0.97886 | 0.30116 | 0.00065185 | 26880.3908 | 0.023725 | 1.6928 | 21.099 | 24.525 | 1.5589 | 0.14059
2025-02-06 05:23 | 0.27836 | 0.31593 | 26.3439 | 0.040221 | 0.97886 | 0.30582 | 0.00066195 | 27296.7527 | 0.023725 | 1.6927 | 21.3798 | 24.8511 | 1.5737 | 0.14193
2025-02-06 05:24 | 0.28802 | 0.32689 | 26.3433 | 0.040401 | 0.97886 | 0.31643 | 0.0006849 | 28243.1428 | 0.023726 | 1.6927 | 22.0158 | 25.59 | 1.6329 | 0.14727
2025-02-06 05:25 | 0.30385 | 0.34485 | 26.3426 | 0.040455 | 0.97886 | 0.33382 | 0.00072255 | 29795.2748 | 0.023726 | 1.6927 | 23.0524 | 26.7945 | 1.7205 | 0.15517
2025-02-06 05:26 | 0.31427 | 0.35668 | 26.3415 | 0.040421 | 0.97886 | 0.34527 | 0.00074734 | 30817.2879 | 0.023727 | 1.6926 | 23.731 | 27.5825 | 1.7751 | 0.16009
2025-02-06 05:27 | 0.27952 | 0.31724 | 26.3398 | 0.040083 | 0.97887 | 0.30709 | 0.00066471 | 27409.7171 | 0.023728 | 1.6926 | 21.4563 | 24.9375 | 1.5744 | 0.14199
2025-02-06 05:28 | 0.26678 | 0.30278 | 26.3381 | 0.040118 | 0.97887 | 0.2931 | 0.00063441 | 26160.1365 | 0.023729 | 1.6925 | 20.6125 | 23.9559 | 1.5072 | 0.13593
2025-02-06 05:29 | 0.26408 | 0.29971 | 26.3363 | 0.039969 | 0.97887 | 0.29013 | 0.00062798 | 25894.8864 | 0.023731 | 1.6924 | 20.4328 | 23.746 | 1.487 | 0.13411
2025-02-06 05:30 | 0.25636 | 0.29094 | 26.3346 | 0.039966 | 0.97888 | 0.28164 | 0.00060962 | 25137.4932 | 0.023732 | 1.6923 | 19.9179 | 23.1467 | 1.4453 | 0.13035
2025-02-06 05:31 | 0.24941 | 0.28306 | 26.334 | 0.039982 | 0.97888 | 0.27401 | 0.00059309 | 24455.9692 | 0.023732 | 1.6923 | 19.4526 | 22.6057 | 1.4085 | 0.12703
2025-02-06 05:32 | 0.24516 | 0.27824 | 26.3346 | 0.039722 | 0.97888 | 0.26934 | 0.000583 | 24039.6195 | 0.023732 | 1.6923 | 19.1674 | 22.2746 | 1.3767 | 0.12416
2025-02-06 05:33 | 0.23165 | 0.2629 | 26.3353 | 0.039594 | 0.97888 | 0.2545 | 0.00055086 | 22714.6801 | 0.023731 | 1.6923 | 18.2553 | 21.2149 | 1.3 | 0.11724
2025-02-06 05:34 | 0.23165 | 0.2629 | 26.3359 | 0.039327 | 0.97887 | 0.2545 | 0.00055086 | 22714.7592 | 0.023731 | 1.6924 | 18.2553 | 21.2153 | 1.2913 | 0.11646
2025-02-06 05:35 | 0.22779 | 0.25852 | 26.3366 | 0.039048 | 0.97887 | 0.25026 | 0.00054168 | 22336.258 | 0.023731 | 1.6924 | 17.9933 | 20.9111 | 1.2617 | 0.11379
2025-02-06 05:36 | 0.22624 | 0.25677 | 26.3373 | 0.038913 | 0.97887 | 0.24856 | 0.00053801 | 22184.9149 | 0.02373 | 1.6924 | 17.8884 | 20.7895 | 1.2493 | 0.11267
2025-02-06 05:37 | 0.22586 | 0.25633 | 26.3382 | 0.038497 | 0.97887 | 0.24814 | 0.00053709 | 22147.159 | 0.023729 | 1.6925 | 17.8621 | 20.7594 | 1.2339 | 0.11129
2025-02-06 05:38 | 0.21003 | 0.23837 | 26.339 | 0.038431 | 0.97887 | 0.23074 | 0.00049945 | 20595.0611 | 0.023729 | 1.6925 | 16.7801 | 19.5023 | 1.1493 | 0.10365
2025-02-06 05:39 | 0.19729 | 0.22391 | 26.3399 | 0.037765 | 0.97887 | 0.21675 | 0.00046915 | 19345.8188 | 0.023728 | 1.6926 | 15.9009 | 18.4808 | 1.0639 | 0.095949
2025-02-06 05:40 | 0.183 | 0.2077 | 26.3407 | 0.036647 | 0.97886 | 0.20105 | 0.00043518 | 17945.128 | 0.023728 | 1.6926 | 14.9056 | 17.3244 | 0.96089 | 0.086661
2025-02-06 05:41 | 0.17065 | 0.19368 | 26.3412 | 0.035868 | 0.97886 | 0.18748 | 0.0004058 | 16733.6844 | 0.023727 | 1.6926 | 14.036 | 16.3138 | 0.87966 | 0.079335
2025-02-06 05:42 | 0.17219 | 0.19543 | 26.3412 | 0.035337 | 0.97886 | 0.18918 | 0.00040947 | 16885.1205 | 0.023727 | 1.6926 | 14.1451 | 16.4407 | 0.87414 | 0.078837
2025-02-06 05:43 | 0.16486 | 0.1871 | 26.3412 | 0.034829 | 0.97886 | 0.18112 | 0.00039203 | 16165.7993 | 0.023727 | 1.6926 | 13.6253 | 15.8366 | 0.82642 | 0.074533
2025-02-06 05:44 | 0.16022 | 0.18185 | 26.3412 | 0.034499 | 0.97886 | 0.17603 | 0.00038101 | 15711.4915 | 0.023727 | 1.6926 | 13.2954 | 15.453 | 0.79657 | 0.071841
2025-02-06 05:45 | 0.14401 | 0.16344 | 26.3412 | 0.033433 | 0.97886 | 0.15821 | 0.00034245 | 14121.4131 | 0.023727 | 1.6926 | 12.1297 | 14.0982 | 0.69701 | 0.062862
2025-02-06 05:46 | 0.13281 | 0.15073 | 26.3412 | 0.03238 | 0.97886 | 0.14591 | 0.00031583 | 13023.5012 | 0.023727 | 1.6926 | 11.3141 | 13.1502 | 0.62468 | 0.056338
2025-02-06 05:47 | 0.14941 | 0.16958 | 26.3412 | 0.031736 | 0.97886 | 0.16415 | 0.00035531 | 14651.4389 | 0.023727 | 1.6926 | 12.5202 | 14.5521 | 0.68538 | 0.061813
2025-02-06 05:48 | 0.15173 | 0.17221 | 26.3414 | 0.030981 | 0.97886 | 0.1667 | 0.00036081 | 14878.6092 | 0.023727 | 1.6926 | 12.6869 | 14.7459 | 0.67902 | 0.061239
2025-02-06 05:49 | 0.14169 | 0.16081 | 26.3418 | 0.030154 | 0.97886 | 0.15567 | 0.00033694 | 13894.3057 | 0.023727 | 1.6926 | 11.9617 | 13.9031 | 0.61897 | 0.055824
2025-02-06 05:50 | 0.14285 | 0.16213 | 26.3423 | 0.029407 | 0.97886 | 0.15694 | 0.0003397 | 14007.916 | 0.023727 | 1.6927 | 12.0457 | 14.0009 | 0.60836 | 0.054866
2025-02-06 05:51 | 0.14826 | 0.16826 | 26.3427 | 0.028809 | 0.97886 | 0.16288 | 0.00035255 | 14537.9791 | 0.023726 | 1.6927 | 12.4367 | 14.4555 | 0.61758 | 0.055698
2025-02-06 05:52 | 0.15019 | 0.17045 | 26.3431 | 0.028045 | 0.97886 | 0.165 | 0.00035714 | 14727.3097 | 0.023726 | 1.6927 | 12.5758 | 14.6174 | 0.60871 | 0.054898
2025-02-06 05:53 | 0.16254 | 0.18448 | 26.3436 | 0.027383 | 0.97886 | 0.17857 | 0.00038652 | 15938.8563 | 0.023726 | 1.6927 | 13.4605 | 15.6459 | 0.64107 | 0.057817
2025-02-06 05:54 | 0.16833 | 0.19105 | 26.3443 | 0.026888 | 0.97886 | 0.18494 | 0.00040029 | 16506.807 | 0.023725 | 1.6928 | 13.8719 | 16.1244 | 0.65093 | 0.058706
2025-02-06 05:55 | 0.16524 | 0.18755 | 26.3449 | 0.026354 | 0.97886 | 0.18154 | 0.00039295 | 16203.9866 | 0.023725 | 1.6928 | 13.6528 | 15.8699 | 0.62681 | 0.056531
2025-02-06 05:56 | 0.18377 | 0.20858 | 26.3456 | 0.02599 | 0.97886 | 0.2019 | 0.00043702 | 18021.3184 | 0.023724 | 1.6928 | 14.9596 | 17.3892 | 0.68431 | 0.061716
2025-02-06 05:57 | 0.19652 | 0.22304 | 26.3462 | 0.025484 | 0.97885 | 0.2159 | 0.00046731 | 19270.7633 | 0.023724 | 1.6928 | 15.8473 | 18.4214 | 0.71536 | 0.064517
2025-02-06 05:58 | 0.19922 | 0.22611 | 26.3466 | 0.025153 | 0.97885 | 0.21887 | 0.00047374 | 19535.8199 | 0.023723 | 1.6929 | 16.0346 | 18.6392 | 0.71536 | 0.064516
2025-02-06 05:59 | 0.20501 | 0.23268 | 26.3466 | 0.025097 | 0.97885 | 0.22523 | 0.00048751 | 20103.7211 | 0.023723 | 1.6929 | 16.4346 | 19.1042 | 0.73358 | 0.06616
2025-02-06 06:00 | 0.21312 | 0.24188 | 26.3466 | 0.024885 | 0.97885 | 0.23414 | 0.00050679 | 20898.7827 | 0.023723 | 1.6929 | 16.9921 | 19.7522 | 0.75482 | 0.068076
2025-02-06 06:01 | 0.21312 | 0.24188 | 26.3466 | 0.024771 | 0.97885 | 0.23414 | 0.00050679 | 20898.7827 | 0.023723 | 1.6929 | 16.9921 | 19.7522 | 0.75135 | 0.067762
2025-02-06 06:02 | 0.22084 | 0.25065 | 26.3466 | 0.024926 | 0.97885 | 0.24262 | 0.00052515 | 21655.9852 | 0.023723 | 1.6929 | 17.5202 | 20.3661 | 0.7822 | 0.070544
2025-02-06 06:03 | 0.22007 | 0.24977 | 26.3466 | 0.025165 | 0.97885 | 0.24177 | 0.00052332 | 21580.2654 | 0.023723 | 1.6929 | 17.4675 | 20.3049 | 0.78704 | 0.070981
2025-02-06 06:04 | 0.21543 | 0.24451 | 26.3466 | 0.025409 | 0.97885 | 0.23668 | 0.0005123 | 21125.9441 | 0.023723 | 1.6929 | 17.1508 | 19.9367 | 0.77871 | 0.07023
2025-02-06 06:05 | 0.23551 | 0.2673 | 26.3464 | 0.025919 | 0.97885 | 0.25874 | 0.00056004 | 23094.6509 | 0.023724 | 1.6928 | 18.5166 | 21.5244 | 0.86482 | 0.077996
2025-02-06 06:06 | 0.22933 | 0.26029 | 26.3461 | 0.026181 | 0.97885 | 0.25195 | 0.00054535 | 22488.8519 | 0.023724 | 1.6928 | 18.0982 | 21.0378 | 0.85167 | 0.07681
2025-02-06 06:07 | 0.20346 | 0.23093 | 26.3458 | 0.026171 | 0.97885 | 0.22353 | 0.00048384 | 19952.1977 | 0.023724 | 1.6928 | 16.3281 | 18.98 | 0.75944 | 0.068492
2025-02-06 06:08 | 0.18995 | 0.21559 | 26.3455 | 0.026342 | 0.97886 | 0.20869 | 0.00045171 | 18627.0682 | 0.023724 | 1.6928 | 15.3911 | 17.8907 | 0.71584 | 0.064559
2025-02-06 06:09 | 0.18995 | 0.21559 | 26.3452 | 0.026695 | 0.97886 | 0.20869 | 0.00045171 | 18627.0373 | 0.023724 | 1.6928 | 15.3911 | 17.8906 | 0.72542 | 0.065424
2025-02-06 06:10 | 0.18416 | 0.20902 | 26.3449 | 0.027285 | 0.97886 | 0.20233 | 0.00043793 | 18059.11 | 0.023725 | 1.6928 | 14.9866 | 17.4203 | 0.71981 | 0.064918
2025-02-06 06:11 | 0.17798 | 0.20201 | 26.3446 | 0.027536 | 0.97886 | 0.19554 | 0.00042325 | 17453.3251 | 0.023725 | 1.6928 | 14.5533 | 16.9165 | 0.70312 | 0.063413
2025-02-06 06:12 | 0.18455 | 0.20945 | 26.3443 | 0.027664 | 0.97886 | 0.20275 | 0.00043885 | 18096.9101 | 0.023725 | 1.6928 | 15.0137 | 17.4515 | 0.73128 | 0.065952
2025-02-06 06:13 | 0.19188 | 0.21778 | 26.344 | 0.028042 | 0.97886 | 0.21081 | 0.0004563 | 18816.2114 | 0.023725 | 1.6927 | 15.5255 | 18.0463 | 0.76938 | 0.069389
2025-02-06 06:14 | 0.19652 | 0.22304 | 26.3437 | 0.028509 | 0.97886 | 0.2159 | 0.00046731 | 19270.4948 | 0.023726 | 1.6927 | 15.8473 | 18.4202 | 0.80022 | 0.07217
2025-02-06 06:15 | 0.1915 | 0.21734 | 26.3433 | 0.028529 | 0.97886 | 0.21039 | 0.00045538 | 18778.2907 | 0.023726 | 1.6927 | 15.4986 | 18.0148 | 0.78124 | 0.070458
2025-02-06 06:16 | 0.18069 | 0.20507 | 26.343 | 0.028825 | 0.97886 | 0.19851 | 0.00042967 | 17718.1962 | 0.023726 | 1.6927 | 14.7431 | 17.1365 | 0.7467 | 0.067343
2025-02-06 06:17 | 0.18648 | 0.21164 | 26.3427 | 0.029203 | 0.97886 | 0.20487 | 0.00044344 | 18286.0561 | 0.023726 | 1.6927 | 15.1486 | 17.6077 | 0.77963 | 0.070313
2025-02-06 06:18 | 0.18686 | 0.21208 | 26.3424 | 0.02933 | 0.97886 | 0.2053 | 0.00044436 | 18323.8845 | 0.023726 | 1.6927 | 15.1756 | 17.6389 | 0.78456 | 0.070758
2025-02-06 06:19 | 0.18184 | 0.20639 | 26.3419 | 0.02937 | 0.97886 | 0.19978 | 0.00043243 | 17831.6685 | 0.023727 | 1.6926 | 14.8244 | 17.2305 | 0.76546 | 0.069035
2025-02-06 06:20 | 0.19574 | 0.22216 | 26.3413 | 0.029135 | 0.97886 | 0.21505 | 0.00046548 | 19194.5319 | 0.023727 | 1.6926 | 15.7938 | 18.357 | 0.81468 | 0.073474
2025-02-06 06:21 | 0.19999 | 0.22698 | 26.3407 | 0.02888 | 0.97887 | 0.21972 | 0.00047558 | 19610.913 | 0.023728 | 1.6926 | 16.088 | 18.6987 | 0.82426 | 0.074338
2025-02-06 06:22 | 0.20231 | 0.22961 | 26.34 | 0.02866 | 0.97887 | 0.22226 | 0.00048109 | 19837.9967 | 0.023728 | 1.6926 | 16.2481 | 18.8845 | 0.82701 | 0.074586
2025-02-06 06:23 | 0.1996 | 0.22654 | 26.3394 | 0.028515 | 0.97887 | 0.21929 | 0.00047466 | 19572.9177 | 0.023729 | 1.6925 | 16.0613 | 18.6671 | 0.81232 | 0.073261
2025-02-06 06:24 | 0.17489 | 0.19849 | 26.3393 | 0.028352 | 0.97887 | 0.19215 | 0.0004159 | 17149.9563 | 0.023729 | 1.6925 | 14.3358 | 16.6616 | 0.71185 | 0.0642
2025-02-06 06:25 | 0.16486 | 0.1871 | 26.3397 | 0.028004 | 0.97887 | 0.18112 | 0.00039203 | 16165.672 | 0.023728 | 1.6926 | 13.6253 | 15.836 | 0.66447 | 0.059927
2025-02-06 06:26 | 0.15636 | 0.17746 | 26.3402 | 0.027638 | 0.97887 | 0.17179 | 0.00037183 | 15332.8187 | 0.023728 | 1.6926 | 13.0194 | 15.1319 | 0.62341 | 0.056224
2025-02-06 06:27 | 0.15405 | 0.17483 | 26.3407 | 0.027272 | 0.97887 | 0.16924 | 0.00036632 | 15105.7034 | 0.023728 | 1.6926 | 12.8533 | 14.9391 | 0.60643 | 0.054693
2025-02-06 06:28 | 0.15829 | 0.17965 | 26.3411 | 0.026856 | 0.97886 | 0.17391 | 0.00037642 | 15522.1898 | 0.023727 | 1.6926 | 13.1575 | 15.2928 | 0.61295 | 0.05528
2025-02-06 06:29 | 0.14131 | 0.16038 | 26.3416 | 0.026333 | 0.97886 | 0.15524 | 0.00033603 | 13856.4284 | 0.023727 | 1.6926 | 11.9336 | 13.8704 | 0.53912 | 0.048622
2025-02-06 06:30 | 0.12123 | 0.13759 | 26.342 | 0.025833 | 0.97886 | 0.13319 | 0.00028828 | 11887.7852 | 0.023727 | 1.6927 | 10.4602 | 12.158 | 0.45664 | 0.041183
2025-02-06 06:31 | 0.12741 | 0.1446 | 26.3423 | 0.025695 | 0.97886 | 0.13997 | 0.00030297 | 12493.5475 | 0.023726 | 1.6927 | 10.9169 | 12.689 | 0.47637 | 0.042962
2025-02-06 06:32 | 0.1359 | 0.15424 | 26.3423 | 0.025296 | 0.97886 | 0.14931 | 0.00032317 | 13326.4507 | 0.023726 | 1.6927 | 11.54 | 13.4131 | 0.4989 | 0.044994
2025-02-06 06:33 | 0.11158 | 0.12664 | 26.3423 | 0.024614 | 0.97886 | 0.12258 | 0.00026533 | 10941.3191 | 0.023726 | 1.6927 | 9.7398 | 11.3208 | 0.40179 | 0.036237
2025-02-06 06:34 | 0.092659 | 0.10516 | 26.3423 | 0.023962 | 0.97886 | 0.1018 | 0.00022034 | 9086.2165 | 0.023726 | 1.6927 | 8.3016 | 9.6491 | 0.32722 | 0.029511
2025-02-06 06:35 | 0.081077 | 0.092019 | 26.3423 | 0.023572 | 0.97886 | 0.089074 | 0.0001928 | 7950.4394 | 0.023726 | 1.6927 | 7.4009 | 8.6023 | 0.2831 | 0.025532
2025-02-06 06:36 | 0.082235 | 0.093334 | 26.3423 | 0.023505 | 0.97886 | 0.090347 | 0.00019556 | 8064.017 | 0.023726 | 1.6927 | 7.4918 | 8.7078 | 0.28617 | 0.025809
2025-02-06 06:37 | 0.093046 | 0.1056 | 26.3423 | 0.023259 | 0.97886 | 0.10222 | 0.00022126 | 9124.0756 | 0.023726 | 1.6927 | 8.3313 | 9.6836 | 0.31889 | 0.02876
2025-02-06 06:38 | 0.068336 | 0.077559 | 26.3423 | 0.02279 | 0.97886 | 0.075077 | 0.0001625 | 6701.0846 | 0.023726 | 1.6927 | 6.389 | 7.4261 | 0.23216 | 0.020938
2025-02-06 06:39 | 0.058298 | 0.066166 | 26.3423 | 0.02154 | 0.97886 | 0.064049 | 0.00013863 | 5716.7445 | 0.023726 | 1.6927 | 5.5731 | 6.4777 | 0.18825 | 0.016978
2025-02-06 06:40 | 0.057526 | 0.06529 | 26.3423 | 0.020119 | 0.97886 | 0.0632 | 0.0001368 | 5641.0261 | 0.023726 | 1.6927 | 5.5096 | 6.4039 | 0.17359 | 0.015655
2025-02-06 06:41 | 0.062159 | 0.070548 | 26.3423 | 0.018988 | 0.97886 | 0.06829 | 0.00014781 | 6095.3367 | 0.023726 | 1.6927 | 5.8891 | 6.845 | 0.17654 | 0.015922
2025-02-06 06:42 | 0.047488 | 0.053897 | 26.3423 | 0.018245 | 0.97886 | 0.052172 | 0.00011293 | 4656.6859 | 0.023726 | 1.6927 | 4.6719 | 5.4303 | 0.1308 | 0.011797
2025-02-06 06:43 | 0.023165 | 0.026291 | 26.3423 | 0.017011 | 0.97886 | 0.02545 | 5.5086e-05 | 2271.5541 | 0.023726 | 1.6927 | 2.5199 | 2.929 | 0.06082 | 0.0054852
2025-02-06 06:44 | 0.030886 | 0.035055 | 26.3423 | 0.015077 | 0.97886 | 0.033933 | 7.3448e-05 | 3028.7388 | 0.023726 | 1.6927 | 3.2273 | 3.7511 | 0.07127 | 0.0064277
2025-02-06 06:45 | 0.041697 | 0.047324 | 26.342 | 0.013398 | 0.97886 | 0.04581 | 9.9155e-05 | 4088.792 | 0.023727 | 1.6927 | 4.1776 | 4.8556 | 0.084702 | 0.0076391
2025-02-06 06:46 | 0.047488 | 0.053897 | 26.3416 | 0.012383 | 0.97886 | 0.052172 | 0.00011293 | 4656.6684 | 0.023727 | 1.6926 | 4.6719 | 5.4302 | 0.088779 | 0.0080067
2025-02-06 06:47 | 0.047874 | 0.054335 | 26.3411 | 0.011895 | 0.97886 | 0.052596 | 0.00011384 | 4694.5159 | 0.023727 | 1.6926 | 4.7046 | 5.4681 | 0.085949 | 0.0077516
2025-02-06 06:48 | 0.050577 | 0.057402 | 26.3407 | 0.011488 | 0.97887 | 0.055565 | 0.00012027 | 4959.5165 | 0.023728 | 1.6926 | 4.9321 | 5.7325 | 0.087531 | 0.0078942
2025-02-06 06:49 | 0.063703 | 0.0723 | 26.3402 | 0.010785 | 0.97887 | 0.069987 | 0.00015149 | 6246.7037 | 0.023728 | 1.6926 | 6.0147 | 6.9907 | 0.10267 | 0.0092593
2025-02-06 06:50 | 0.071039 | 0.080625 | 26.3397 | 0.010545 | 0.97887 | 0.078046 | 0.00016893 | 6966.0038 | 0.023728 | 1.6926 | 6.6057 | 7.6775 | 0.1115 | 0.010056
2025-02-06 06:51 | 0.10231 | 0.11612 | 26.3393 | 0.010645 | 0.97887 | 0.1124 | 0.0002433 | 10032.5347 | 0.023729 | 1.6925 | 9.04 | 10.5067 | 0.15988 | 0.014419
2025-02-06 06:52 | 0.11196 | 0.12707 | 26.3387 | 0.01041 | 0.97887 | 0.12301 | 0.00026625 | 10978.9671 | 0.023729 | 1.6925 | 9.7688 | 11.3535 | 0.17048 | 0.015375
2025-02-06 06:53 | 0.12779 | 0.14504 | 26.3381 | 0.011414 | 0.97887 | 0.1404 | 0.00030389 | 12531.1223 | 0.023729 | 1.6925 | 10.9454 | 12.7207 | 0.2122 | 0.019137
2025-02-06 06:54 | 0.15752 | 0.17878 | 26.3374 | 0.011602 | 0.97887 | 0.17306 | 0.00037459 | 15446.1636 | 0.02373 | 1.6924 | 13.1023 | 15.2273 | 0.26353 | 0.023767
2025-02-06 06:55 | 0.16717 | 0.18973 | 26.3368 | 0.010689 | 0.97887 | 0.18366 | 0.00039754 | 16392.5624 | 0.02373 | 1.6924 | 13.7898 | 16.0261 | 0.25701 | 0.023179
2025-02-06 06:56 | 0.18069 | 0.20506 | 26.3361 | 0.0099544 | 0.97887 | 0.19851 | 0.00042967 | 17717.5344 | 0.023731 | 1.6924 | 14.7431 | 17.1337 | 0.25781 | 0.023251
2025-02-06 06:57 | 0.18648 | 0.21164 | 26.3358 | 0.009334 | 0.97887 | 0.20487 | 0.00044344 | 18285.3737 | 0.023731 | 1.6924 | 15.1486 | 17.6048 | 0.24914 | 0.022469
2025-02-06 06:58 | 0.20231 | 0.2296 | 26.3358 | 0.0092262 | 0.97887 | 0.22226 | 0.00048109 | 19837.5477 | 0.023731 | 1.6924 | 16.2481 | 18.8826 | 0.2662 | 0.024008
2025-02-06 06:59 | 0.21505 | 0.24406 | 26.3358 | 0.0092794 | 0.97887 | 0.23626 | 0.00051138 | 21086.859 | 0.023731 | 1.6924 | 17.1244 | 19.9009 | 0.28381 | 0.025596
2025-02-06 07:00 | 0.21775 | 0.24713 | 26.3358 | 0.0095817 | 0.97887 | 0.23923 | 0.00051781 | 21351.8642 | 0.023731 | 1.6924 | 17.3093 | 20.1158 | 0.29657 | 0.026747
2025-02-06 07:01 | 0.21196 | 0.24056 | 26.3358 | 0.010153 | 0.97887 | 0.23287 | 0.00050404 | 20783.996 | 0.023731 | 1.6924 | 16.9126 | 19.6549 | 0.30626 | 0.027621
2025-02-06 07:02 | 0.20385 | 0.23135 | 26.3358 | 0.011073 | 0.97887 | 0.22396 | 0.00048476 | 19988.9805 | 0.023731 | 1.6924 | 16.3548 | 19.0065 | 0.32181 | 0.029023
2025-02-06 07:03 | 0.20192 | 0.22916 | 26.3358 | 0.012191 | 0.97887 | 0.22184 | 0.00048017 | 19799.6911 | 0.023731 | 1.6924 | 16.2215 | 18.8516 | 0.35111 | 0.031666
2025-02-06 07:04 | 0.19922 | 0.2261 | 26.3353 | 0.013441 | 0.97888 | 0.21887 | 0.00047374 | 19534.6255 | 0.023731 | 1.6923 | 16.0346 | 18.6342 | 0.38215 | 0.034466
2025-02-06 07:05 | 0.1915 | 0.21733 | 26.3342 | 0.014932 | 0.97888 | 0.21039 | 0.00045538 | 18777.3603 | 0.023732 | 1.6923 | 15.4986 | 18.0109 | 0.40878 | 0.036867
2025-02-06 07:06 | 0.18841 | 0.21382 | 26.3331 | 0.016636 | 0.97888 | 0.20699 | 0.00044803 | 18474.3923 | 0.023733 | 1.6923 | 15.2834 | 17.7603 | 0.44839 | 0.040439
2025-02-06 07:07 | 0.19922 | 0.22609 | 26.332 | 0.018334 | 0.97888 | 0.21887 | 0.00047374 | 19534.2853 | 0.023734 | 1.6922 | 16.0346 | 18.6328 | 0.5212 | 0.047006
2025-02-06 07:08 | 0.19536 | 0.22171 | 26.331 | 0.020009 | 0.97888 | 0.21463 | 0.00046456 | 19155.6021 | 0.023734 | 1.6922 | 15.767 | 18.3213 | 0.55828 | 0.05035
2025-02-06 07:09 | 0.18609 | 0.21119 | 26.3297 | 0.021871 | 0.97889 | 0.20445 | 0.00044253 | 18246.9069 | 0.023735 | 1.6921 | 15.1217 | 17.5709 | 0.58252 | 0.052536
2025-02-06 07:10 | 0.1942 | 0.22039 | 26.3282 | 0.023645 | 0.97889 | 0.21335 | 0.00046181 | 19041.7415 | 0.023736 | 1.692 | 15.6865 | 18.2267 | 0.65593 | 0.059157
2025-02-06 07:11 | 0.20733 | 0.23529 | 26.3266 | 0.025287 | 0.97889 | 0.22778 | 0.00049302 | 20328.6916 | 0.023738 | 1.692 | 16.5942 | 19.2806 | 0.74668 | 0.067341
2025-02-06 07:12 | 0.19729 | 0.22389 | 26.3251 | 0.026875 | 0.9789 | 0.21675 | 0.00046915 | 19344.277 | 0.023739 | 1.6919 | 15.9009 | 18.4744 | 0.75678 | 0.068253
2025-02-06 07:13 | 0.183 | 0.20768 | 26.3236 | 0.02844 | 0.9789 | 0.20105 | 0.00043518 | 17943.468 | 0.02374 | 1.6918 | 14.9056 | 17.3173 | 0.74532 | 0.067219
2025-02-06 07:14 | 0.17644 | 0.20023 | 26.3232 | 0.029765 | 0.9789 | 0.19384 | 0.00041957 | 17299.8848 | 0.02374 | 1.6918 | 14.4446 | 16.7817 | 0.75328 | 0.067936
2025-02-06 07:15 | 0.18609 | 0.21118 | 26.3236 | 0.030673 | 0.9789 | 0.20445 | 0.00044253 | 18246.3107 | 0.02374 | 1.6918 | 15.1217 | 17.5684 | 0.81681 | 0.073666
2025-02-06 07:16 | 0.18455 | 0.20943 | 26.3241 | 0.0316 | 0.9789 | 0.20275 | 0.00043885 | 18094.9312 | 0.023739 | 1.6918 | 15.0137 | 17.4431 | 0.83483 | 0.075292
2025-02-06 07:17 | 0.17837 | 0.20242 | 26.3245 | 0.032466 | 0.9789 | 0.19596 | 0.00042416 | 17489.2834 | 0.023739 | 1.6919 | 14.5804 | 16.94 | 0.83023 | 0.074877
2025-02-06 07:18 | 0.15829 | 0.17964 | 26.3249 | 0.033239 | 0.9789 | 0.17391 | 0.00037642 | 15520.8288 | 0.023739 | 1.6919 | 13.1575 | 15.2869 | 0.75827 | 0.068386
2025-02-06 07:19 | 0.15096 | 0.17131 | 26.3242 | 0.033896 | 0.9789 | 0.16585 | 0.00035898 | 14801.5108 | 0.023739 | 1.6919 | 12.6314 | 14.6754 | 0.7389 | 0.06664
2025-02-06 07:20 | 0.15405 | 0.17482 | 26.3224 | 0.034382 | 0.9789 | 0.16924 | 0.00036632 | 15104.2149 | 0.023741 | 1.6918 | 12.8533 | 14.9326 | 0.76413 | 0.068915
2025-02-06 07:21 | 0.16215 | 0.18402 | 26.3207 | 0.034842 | 0.97891 | 0.17815 | 0.0003856 | 15899.0259 | 0.023742 | 1.6917 | 13.433 | 15.6055 | 0.81329 | 0.073348
2025-02-06 07:22 | 0.16215 | 0.18401 | 26.319 | 0.035252 | 0.97891 | 0.17815 | 0.0003856 | 15898.8783 | 0.023743 | 1.6916 | 13.433 | 15.6048 | 0.8228 | 0.074206
2025-02-06 07:23 | 0.16215 | 0.18401 | 26.3173 | 0.035631 | 0.97891 | 0.17815 | 0.0003856 | 15898.7307 | 0.023744 | 1.6915 | 13.433 | 15.6042 | 0.83161 | 0.075001
2025-02-06 07:24 | 0.16215 | 0.18401 | 26.3157 | 0.035946 | 0.97892 | 0.17815 | 0.0003856 | 15898.593 | 0.023745 | 1.6915 | 13.433 | 15.6036 | 0.83892 | 0.07566
2025-02-06 07:25 | 0.18339 | 0.20811 | 26.3142 | 0.03626 | 0.97892 | 0.20148 | 0.0004361 | 17980.4048 | 0.023746 | 1.6914 | 14.9326 | 17.3449 | 0.9519 | 0.08585
2025-02-06 07:26 | 0.19767 | 0.22432 | 26.3127 | 0.036427 | 0.97892 | 0.21717 | 0.00047007 | 19380.8256 | 0.023747 | 1.6913 | 15.9276 | 18.5 | 1.0273 | 0.09265
2025-02-06 07:27 | 0.1857 | 0.21073 | 26.3112 | 0.03656 | 0.97892 | 0.20402 | 0.00044161 | 18207.2294 | 0.023749 | 1.6913 | 15.0947 | 17.5319 | 0.97128 | 0.087597
2025-02-06 07:28 | 0.19922 | 0.22606 | 26.3097 | 0.036757 | 0.97893 | 0.21887 | 0.00047374 | 19531.9212 | 0.02375 | 1.6912 | 16.0346 | 18.6229 | 1.0443 | 0.09418
2025-02-06 07:29 | 0.20501 | 0.23263 | 26.3084 | 0.036629 | 0.97893 | 0.22523 | 0.00048751 | 20099.572 | 0.02375 | 1.6911 | 16.4346 | 19.0869 | 1.0694 | 0.096451
2025-02-06 07:30 | 0.20346 | 0.23088 | 26.3073 | 0.03665 | 0.97893 | 0.22353 | 0.00048384 | 19948.0463 | 0.023751 | 1.6911 | 16.3281 | 18.9627 | 1.0623 | 0.095809
2025-02-06 07:31 | 0.18995 | 0.21555 | 26.3063 | 0.036722 | 0.97893 | 0.20869 | 0.00045171 | 18623.1154 | 0.023752 | 1.6911 | 15.3911 | 17.874 | 0.99674 | 0.089894
2025-02-06 07:32 | 0.1996 | 0.2265 | 26.3052 | 0.03671 | 0.97894 | 0.21929 | 0.00047466 | 19569.2985 | 0.023753 | 1.691 | 16.0613 | 18.6519 | 1.0447 | 0.094219
2025-02-06 07:33 | 0.20926 | 0.23745 | 26.3041 | 0.036894 | 0.97894 | 0.2299 | 0.00049761 | 20515.4709 | 0.023754 | 1.691 | 16.727 | 19.4245 | 1.0983 | 0.099057
2025-02-06 07:34 | 0.20771 | 0.23569 | 26.3039 | 0.036941 | 0.97894 | 0.2282 | 0.00049394 | 20364.041 | 0.023754 | 1.6909 | 16.6208 | 19.3011 | 1.092 | 0.098485
2025-02-06 07:35 | 0.20926 | 0.23745 | 26.3043 | 0.03696 | 0.97894 | 0.2299 | 0.00049761 | 20515.4939 | 0.023753 | 1.691 | 16.727 | 19.4246 | 1.1003 | 0.099235
2025-02-06 07:36 | 0.20192 | 0.22912 | 26.3047 | 0.036935 | 0.97894 | 0.22184 | 0.00048017 | 19796.3627 | 0.023753 | 1.691 | 16.2215 | 18.8377 | 1.0627 | 0.095847
2025-02-06 07:37 | 0.20501 | 0.23263 | 26.3052 | 0.03679 | 0.97894 | 0.22523 | 0.00048751 | 20099.2215 | 0.023753 | 1.691 | 16.4346 | 19.0855 | 1.0741 | 0.096867
2025-02-06 07:38 | 0.21698 | 0.24621 | 26.3056 | 0.036772 | 0.97894 | 0.23838 | 0.00051597 | 21272.6715 | 0.023752 | 1.691 | 17.2565 | 20.0401 | 1.1333 | 0.10221
2025-02-06 07:39 | 0.22045 | 0.25015 | 26.3046 | 0.03682 | 0.97894 | 0.2422 | 0.00052424 | 21613.2167 | 0.023753 | 1.691 | 17.4939 | 20.3153 | 1.1521 | 0.1039
2025-02-06 07:40 | 0.21582 | 0.24489 | 26.3024 | 0.036871 | 0.97894 | 0.23711 | 0.00051322 | 21158.7522 | 0.023755 | 1.6909 | 17.1772 | 19.9465 | 1.1305 | 0.10195
2025-02-06 07:41 | 0.21698 | 0.2462 | 26.3003 | 0.037014 | 0.97895 | 0.23838 | 0.00051597 | 21272.0594 | 0.023756 | 1.6908 | 17.2565 | 20.0376 | 1.1406 | 0.10287
2025-02-06 07:42 | 0.22624 | 0.25672 | 26.2981 | 0.037002 | 0.97895 | 0.24856 | 0.00053801 | 22180.2179 | 0.023758 | 1.6907 | 17.8884 | 20.7702 | 1.1866 | 0.10701
2025-02-06 07:43 | 0.23937 | 0.27161 | 26.296 | 0.037003 | 0.97896 | 0.26298 | 0.00056922 | 23466.8522 | 0.023759 | 1.6906 | 18.7774 | 21.8014 | 1.2521 | 0.11292
2025-02-06 07:44 | 0.24825 | 0.28168 | 26.2947 | 0.036884 | 0.97896 | 0.27274 | 0.00059034 | 24337.2266 | 0.02376 | 1.6905 | 19.3749 | 22.4944 | 1.2921 | 0.11654
2025-02-06 07:45 | 0.2359 | 0.26766 | 26.2941 | 0.036873 | 0.97896 | 0.25916 | 0.00056096 | 23125.9622 | 0.023761 | 1.6905 | 18.5428 | 21.5279 | 1.2304 | 0.11096
2025-02-06 07:46 | 0.2359 | 0.26766 | 26.2934 | 0.037014 | 0.97896 | 0.25916 | 0.00056096 | 23125.8811 | 0.023761 | 1.6905 | 18.5428 | 21.5276 | 1.235 | 0.11139
2025-02-06 07:47 | 0.25288 | 0.28693 | 26.2928 | 0.036973 | 0.97896 | 0.27783 | 0.00060136 | 24791.1604 | 0.023762 | 1.6904 | 19.6855 | 22.854 | 1.3182 | 0.11889
2025-02-06 07:48 | 0.25211 | 0.28606 | 26.2921 | 0.037092 | 0.97896 | 0.27698 | 0.00059952 | 24715.3759 | 0.023762 | 1.6904 | 19.6338 | 22.7936 | 1.3186 | 0.11892
2025-02-06 07:49 | 0.24902 | 0.28255 | 26.2906 | 0.036957 | 0.97897 | 0.27359 | 0.00059218 | 24412.3828 | 0.023763 | 1.6903 | 19.4267 | 22.5524 | 1.2984 | 0.1171
2025-02-06 07:50 | 0.23705 | 0.26897 | 26.2884 | 0.036917 | 0.97897 | 0.26044 | 0.00056371 | 23238.8048 | 0.023765 | 1.6903 | 18.621 | 21.6159 | 1.2374 | 0.1116
2025-02-06 07:51 | 0.23937 | 0.27159 | 26.2863 | 0.037003 | 0.97898 | 0.26298 | 0.00056922 | 23465.6226 | 0.023766 | 1.6902 | 18.7774 | 21.7964 | 1.2518 | 0.11289
2025-02-06 07:52 | 0.24246 | 0.27509 | 26.2842 | 0.037172 | 0.97898 | 0.26637 | 0.00057657 | 23768.1292 | 0.023768 | 1.6901 | 18.9856 | 22.0369 | 1.2728 | 0.11479
2025-02-06 07:53 | 0.23937 | 0.27159 | 26.282 | 0.037421 | 0.97898 | 0.26298 | 0.00056922 | 23465.0782 | 0.023769 | 1.69 | 18.7774 | 21.7942 | 1.2657 | 0.11415
2025-02-06 07:54 | 0.25211 | 0.28604 | 26.2821 | 0.037458 | 0.97898 | 0.27698 | 0.00059952 | 24714.0403 | 0.023769 | 1.69 | 19.6338 | 22.7882 | 1.3312 | 0.12006
2025-02-06 07:55 | 0.25288 | 0.28692 | 26.2838 | 0.037321 | 0.97898 | 0.27783 | 0.00060136 | 24789.9641 | 0.023768 | 1.69 | 19.6855 | 22.8491 | 1.3303 | 0.11998
2025-02-06 07:56 | 0.24632 | 0.27948 | 26.2855 | 0.037469 | 0.97898 | 0.27062 | 0.00058575 | 24146.7843 | 0.023767 | 1.6901 | 19.2453 | 22.3391 | 1.3026 | 0.11747
2025-02-06 07:57 | 0.23705 | 0.26897 | 26.2873 | 0.037507 | 0.97897 | 0.26044 | 0.00056371 | 23238.6566 | 0.023765 | 1.6902 | 18.621 | 21.6153 | 1.2571 | 0.11338
2025-02-06 07:58 | 0.2413 | 0.27379 | 26.289 | 0.037391 | 0.97897 | 0.2651 | 0.00057381 | 23655.2043 | 0.023764 | 1.6903 | 18.9076 | 21.9489 | 1.2747 | 0.11496
2025-02-06 07:59 | 0.2664 | 0.30226 | 26.2896 | 0.037288 | 0.97897 | 0.29267 | 0.00063349 | 26115.4287 | 0.023764 | 1.6903 | 20.5868 | 23.8985 | 1.3969 | 0.12599
2025-02-06 08:00 | 0.27682 | 0.31409 | 26.2894 | 0.037299 | 0.97897 | 0.30413 | 0.00065828 | 27137.3057 | 0.023764 | 1.6903 | 21.2777 | 24.7005 | 1.4494 | 0.13072
2025-02-06 08:01 | 0.26678 | 0.3027 | 26.2891 | 0.03738 | 0.97897 | 0.2931 | 0.00063441 | 26153.2169 | 0.023764 | 1.6903 | 20.6125 | 23.9281 | 1.4023 | 0.12647
2025-02-06 08:02 | 0.27952 | 0.31715 | 26.2889 | 0.037439 | 0.97897 | 0.30709 | 0.00066471 | 27402.1804 | 0.023764 | 1.6903 | 21.4563 | 24.9075 | 1.4683 | 0.13243
2025-02-06 08:03 | 0.29342 | 0.33292 | 26.2887 | 0.037448 | 0.97897 | 0.32236 | 0.00069776 | 28764.6867 | 0.023764 | 1.6903 | 22.3706 | 25.9688 | 1.5381 | 0.13872
2025-02-06 08:04 | 0.29033 | 0.32942 | 26.2879 | 0.037384 | 0.97897 | 0.31897 | 0.00069041 | 28461.7708 | 0.023765 | 1.6902 | 22.168 | 25.733 | 1.5201 | 0.13709
2025-02-06 08:05 | 0.28956 | 0.32854 | 26.2866 | 0.037431 | 0.97897 | 0.31812 | 0.00068858 | 28385.8768 | 0.023766 | 1.6902 | 22.1173 | 25.6734 | 1.5181 | 0.13691
2025-02-06 08:06 | 0.27721 | 0.31452 | 26.2853 | 0.037522 | 0.97898 | 0.30455 | 0.0006592 | 27174.5561 | 0.023767 | 1.6901 | 21.3032 | 24.7277 | 1.4598 | 0.13166
2025-02-06 08:07 | 0.28647 | 0.32503 | 26.284 | 0.037556 | 0.97898 | 0.31473 | 0.00068123 | 28082.7018 | 0.023768 | 1.6901 | 21.9142 | 25.4361 | 1.5076 | 0.13596
2025-02-06 08:08 | 0.28609 | 0.32459 | 26.2827 | 0.037715 | 0.97898 | 0.31431 | 0.00068031 | 28044.6603 | 0.023769 | 1.69 | 21.8888 | 25.4059 | 1.512 | 0.13636
2025-02-06 08:09 | 0.27605 | 0.3132 | 26.2833 | 0.037624 | 0.97898 | 0.30328 | 0.00065644 | 27060.7295 | 0.023768 | 1.69 | 21.2267 | 24.6377 | 1.4579 | 0.13148
2025-02-06 08:10 | 0.27914 | 0.31671 | 26.2853 | 0.037863 | 0.97898 | 0.30667 | 0.00066379 | 27363.7922 | 0.023767 | 1.6901 | 21.4308 | 24.8757 | 1.4828 | 0.13373
2025-02-06 08:11 | 0.28531 | 0.32372 | 26.2872 | 0.037907 | 0.97897 | 0.31346 | 0.00067848 | 27969.6447 | 0.023765 | 1.6902 | 21.838 | 25.3496 | 1.5159 | 0.13672
2025-02-06 08:12 | 0.27103 | 0.30752 | 26.2891 | 0.037914 | 0.97897 | 0.29776 | 0.00064451 | 26569.5478 | 0.023764 | 1.6903 | 20.8943 | 24.2553 | 1.4439 | 0.13022
2025-02-06 08:13 | 0.26833 | 0.30445 | 26.2911 | 0.037898 | 0.97897 | 0.29479 | 0.00063808 | 26304.8825 | 0.023763 | 1.6904 | 20.715 | 24.0482 | 1.4297 | 0.12894
2025-02-06 08:14 | 0.28145 | 0.31935 | 26.291 | 0.037996 | 0.97897 | 0.30922 | 0.0006693 | 27591.7333 | 0.023763 | 1.6904 | 21.5836 | 25.0566 | 1.5001 | 0.13529
2025-02-06 08:15 | 0.26948 | 0.30577 | 26.2896 | 0.038197 | 0.97897 | 0.29607 | 0.00064084 | 26418.2254 | 0.023764 | 1.6903 | 20.7919 | 24.1367 | 1.4468 | 0.13049
2025-02-06 08:16 | 0.26794 | 0.30401 | 26.2883 | 0.038187 | 0.97897 | 0.29437 | 0.00063716 | 26266.6355 | 0.023765 | 1.6902 | 20.6894 | 24.0169 | 1.4385 | 0.12973
2025-02-06 08:17 | 0.26176 | 0.297 | 26.2869 | 0.038103 | 0.97897 | 0.28758 | 0.00062247 | 25660.8743 | 0.023766 | 1.6902 | 20.2785 | 23.5392 | 1.4037 | 0.1266
2025-02-06 08:18 | 0.2552 | 0.28955 | 26.2855 | 0.03821 | 0.97898 | 0.28037 | 0.00060687 | 25017.2737 | 0.023767 | 1.6901 | 19.8405 | 23.0299 | 1.3739 | 0.12391
2025-02-06 08:19 | 0.2745 | 0.31145 | 26.2841 | 0.038193 | 0.97898 | 0.30158 | 0.00065277 | 26909.4533 | 0.023768 | 1.6901 | 21.1245 | 24.5196 | 1.4721 | 0.13276
2025-02-06 08:20 | 0.28261 | 0.32065 | 26.2827 | 0.038204 | 0.97898 | 0.31049 | 0.00067205 | 27704.041 | 0.023769 | 1.69 | 21.66 | 25.1403 | 1.5138 | 0.13653
2025-02-06 08:21 | 0.27489 | 0.31189 | 26.283 | 0.038257 | 0.97898 | 0.302 | 0.00065369 | 26947.1313 | 0.023769 | 1.69 | 21.1501 | 24.5485 | 1.4765 | 0.13316
2025-02-06 08:22 | 0.26794 | 0.30401 | 26.2843 | 0.038401 | 0.97898 | 0.29437 | 0.00063716 | 26266.0673 | 0.023768 | 1.6901 | 20.6894 | 24.0146 | 1.4464 | 0.13044
2025-02-06 08:23 | 0.26562 | 0.30138 | 26.2855 | 0.038383 | 0.97898 | 0.29182 | 0.00063165 | 26039.1656 | 0.023767 | 1.6901 | 20.5355 | 23.8367 | 1.4338 | 0.12931
2025-02-06 08:24 | 0.2664 | 0.30226 | 26.2868 | 0.038404 | 0.97897 | 0.29267 | 0.00063349 | 26115.0428 | 0.023766 | 1.6902 | 20.5868 | 23.897 | 1.4386 | 0.12975
2025-02-06 08:25 | 0.27682 | 0.31409 | 26.2881 | 0.038572 | 0.97897 | 0.30413 | 0.00065828 | 27137.1248 | 0.023765 | 1.6902 | 21.2777 | 24.6998 | 1.4988 | 0.13518
2025-02-06 08:26 | 0.2745 | 0.31146 | 26.2888 | 0.038421 | 0.97897 | 0.30158 | 0.00065277 | 26910.1364 | 0.023764 | 1.6903 | 21.1245 | 24.5223 | 1.4811 | 0.13357
2025-02-06 08:27 | 0.29612 | 0.33599 | 26.2891 | 0.038251 | 0.97897 | 0.32533 | 0.00070418 | 29029.6887 | 0.023764 | 1.6903 | 22.5477 | 26.1746 | 1.5849 | 0.14294
2025-02-06 08:28 | 0.30925 | 0.35089 | 26.2894 | 0.038255 | 0.97897 | 0.33975 | 0.0007354 | 30316.5834 | 0.023764 | 1.6903 | 23.4047 | 27.1696 | 1.6519 | 0.14898
2025-02-06 08:29 | 0.29728 | 0.33731 | 26.2897 | 0.038328 | 0.97897 | 0.32661 | 0.00070694 | 29143.3306 | 0.023764 | 1.6903 | 22.6236 | 26.263 | 1.594 | 0.14376
2025-02-06 08:30 | 0.28223 | 0.32022 | 26.29 | 0.038247 | 0.97897 | 0.31006 | 0.00067113 | 27667.2862 | 0.023763 | 1.6903 | 21.6345 | 25.1151 | 1.5139 | 0.13653
2025-02-06 08:31 | 0.26292 | 0.29832 | 26.2903 | 0.038176 | 0.97897 | 0.28886 | 0.00062523 | 25774.9013 | 0.023763 | 1.6903 | 20.3557 | 23.6306 | 1.4125 | 0.12739
2025-02-06 08:32 | 0.25288 | 0.28693 | 26.2907 | 0.038137 | 0.97897 | 0.27783 | 0.00060136 | 24790.8786 | 0.023763 | 1.6904 | 19.6855 | 22.8528 | 1.3596 | 0.12262
2025-02-06 08:33 | 0.24246 | 0.2751 | 26.2912 | 0.038238 | 0.97897 | 0.26637 | 0.00057657 | 23769.0304 | 0.023763 | 1.6904 | 18.9856 | 22.0406 | 1.3096 | 0.11811
2025-02-06 08:34 | 0.21814 | 0.24751 | 26.2918 | 0.038446 | 0.97896 | 0.23965 | 0.00051873 | 21384.6321 | 0.023762 | 1.6904 | 17.3357 | 20.1255 | 1.1905 | 0.10736
2025-02-06 08:35 | 0.19729 | 0.22385 | 26.2925 | 0.038583 | 0.97896 | 0.21675 | 0.00046915 | 19340.8583 | 0.023762 | 1.6904 | 15.9009 | 18.46 | 1.0854 | 0.097893
2025-02-06 08:36 | 0.20424 | 0.23174 | 26.2931 | 0.038782 | 0.97896 | 0.22438 | 0.00048568 | 20022.2096 | 0.023761 | 1.6905 | 16.3814 | 19.0182 | 1.1277 | 0.10171
2025-02-06 08:37 | 0.20231 | 0.22955 | 26.2937 | 0.038951 | 0.97896 | 0.22226 | 0.00048109 | 19833.0336 | 0.023761 | 1.6905 | 16.2481 | 18.8638 | 1.1224 | 0.10123
2025-02-06 08:38 | 0.17876 | 0.20283 | 26.2947 | 0.039126 | 0.97896 | 0.19639 | 0.00042508 | 17524.3127 | 0.02376 | 1.6905 | 14.6076 | 16.9595 | 1.0017 | 0.090345
2025-02-06 08:39 | 0.16061 | 0.18224 | 26.2957 | 0.039257 | 0.97896 | 0.17645 | 0.00038193 | 15745.4782 | 0.023759 | 1.6906 | 13.3229 | 15.4684 | 0.90732 | 0.081829
2025-02-06 08:40 | 0.1332 | 0.15114 | 26.2968 | 0.039575 | 0.97895 | 0.14634 | 0.00031675 | 13058.2252 | 0.023759 | 1.6906 | 11.3424 | 13.1692 | 0.76462 | 0.068959
2025-02-06 08:41 | 0.13281 | 0.1507 | 26.2979 | 0.040093 | 0.97895 | 0.14591 | 0.00031583 | 13020.4509 | 0.023758 | 1.6907 | 11.3141 | 13.1367 | 0.77249 | 0.069669
2025-02-06 08:42 | 0.12239 | 0.13887 | 26.299 | 0.040939 | 0.97895 | 0.13446 | 0.00029104 | 11998.5669 | 0.023757 | 1.6907 | 10.546 | 12.2453 | 0.72935 | 0.065778
2025-02-06 08:43 | 0.069495 | 0.078856 | 26.3004 | 0.041822 | 0.97895 | 0.076349 | 0.00016526 | 6813.1209 | 0.023756 | 1.6908 | 6.4821 | 7.5267 | 0.43245 | 0.039002
2025-02-06 08:44 | 0.042855 | 0.048628 | 26.3022 | 0.043689 | 0.97894 | 0.047082 | 0.00010191 | 4201.4636 | 0.023755 | 1.6909 | 4.2772 | 4.9667 | 0.28328 | 0.025548
2025-02-06 08:45 | 0.050963 | 0.057828 | 26.3039 | 0.044985 | 0.97894 | 0.05599 | 0.00012119 | 4996.3815 | 0.023754 | 1.6909 | 4.9645 | 5.765 | 0.34489 | 0.031105
2025-02-06 08:46 | 0.045171 | 0.051258 | 26.3056 | 0.046383 | 0.97894 | 0.049627 | 0.00010742 | 4428.652 | 0.023752 | 1.691 | 4.4753 | 5.1972 | 0.31649 | 0.028543
2025-02-06 08:47 | 0.035133 | 0.039867 | 26.3073 | 0.047476 | 0.97893 | 0.038599 | 8.3547e-05 | 3444.5389 | 0.023751 | 1.6911 | 3.6054 | 4.1872 | 0.25402 | 0.022909
2025-02-06 08:48 | 0.018918 | 0.021467 | 26.3086 | 0.048402 | 0.97893 | 0.020784 | 4.4987e-05 | 1854.7649 | 0.02375 | 1.6912 | 2.1171 | 2.4588 | 0.14196 | 0.012803
2025-02-06 08:49 | 0 | 0 | 26.3097 | 0.049907 | 0.97893 | 0 | 0 | 0 | 0.02375 | 1.6912 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:50 | 0 | 0 | 26.3108 | 0.050936 | 0.97893 | 0 | 0 | 0 | 0.023749 | 1.6913 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:51 | 0 | 0 | 26.3118 | 0.05175 | 0.97892 | 0 | 0 | 0 | 0.023748 | 1.6913 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:52 | 0 | 0 | 26.3129 | 0.053537 | 0.97892 | 0 | 0 | 0 | 0.023747 | 1.6913 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:53 | 0 | 0 | 26.314 | 0.054308 | 0.97892 | 0 | 0 | 0 | 0.023747 | 1.6914 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:54 | 0 | 0 | 26.3151 | 0.055045 | 0.97892 | 0 | 0 | 0 | 0.023746 | 1.6914 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:55 | 0 | 0 | 26.3161 | 0.05609 | 0.97891 | 0 | 0 | 0 | 0.023745 | 1.6915 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:56 | 0 | 0 | 26.3172 | 0.057383 | 0.97891 | 0 | 0 | 0 | 0.023744 | 1.6915 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:57 | 0 | 0 | 26.3183 | 0.060183 | 0.97891 | 0 | 0 | 0 | 0.023743 | 1.6916 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:58 | 0 | 0 | 26.3198 | 0.060099 | 0.97891 | 0 | 0 | 0 | 0.023742 | 1.6917 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 08:59 | 0 | 0 | 26.3215 | 0.058883 | 0.9789 | 0 | 0 | 0 | 0.023741 | 1.6917 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:00 | 0 | 0 | 26.3232 | 0.057256 | 0.9789 | 0 | 0 | 0 | 0.02374 | 1.6918 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:01 | 0 | 0 | 26.3249 | 0.056263 | 0.9789 | 0 | 0 | 0 | 0.023739 | 1.6919 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:02 | 0 | 0 | 26.3266 | 0.057402 | 0.97889 | 0 | 0 | 0 | 0.023738 | 1.692 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:03 | 0 | 0 | 26.3274 | 0.058723 | 0.97889 | 0 | 0 | 0 | 0.023737 | 1.692 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:04 | 0 | 0 | 26.3276 | 0.05803 | 0.97889 | 0 | 0 | 0 | 0.023737 | 1.692 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:05 | 0 | 0 | 26.3278 | 0.056198 | 0.97889 | 0 | 0 | 0 | 0.023737 | 1.692 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:06 | 0 | 0 | 26.328 | 0.054267 | 0.97889 | 0 | 0 | 0 | 0.023737 | 1.692 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:07 | 0 | 0 | 26.3282 | 0.052689 | 0.97889 | 0 | 0 | 0 | 0.023736 | 1.692 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:08 | 0 | 0 | 26.3293 | 0.051172 | 0.97889 | 0 | 0 | 0 | 0.023736 | 1.6921 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:09 | 0 | 0 | 26.331 | 0.049506 | 0.97888 | 0 | 0 | 0 | 0.023734 | 1.6922 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:10 | 0 | 0 | 26.3328 | 0.048451 | 0.97888 | 0 | 0 | 0 | 0.023733 | 1.6922 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:11 | 0 | 0 | 26.3345 | 0.047654 | 0.97888 | 0 | 0 | 0 | 0.023732 | 1.6923 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:12 | 0 | 0 | 26.3362 | 0.047023 | 0.97887 | 0 | 0 | 0 | 0.023731 | 1.6924 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:13 | 0 | 0 | 26.3373 | 0.045261 | 0.97887 | 0 | 0 | 0 | 0.02373 | 1.6924 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:14 | 0 | 0 | 26.3379 | 0.04355 | 0.97887 | 0 | 0 | 0 | 0.02373 | 1.6925 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:15 | 0 | 0 | 26.3386 | 0.041992 | 0.97887 | 0 | 0 | 0 | 0.023729 | 1.6925 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:16 | 0 | 0 | 26.3392 | 0.040499 | 0.97887 | 0 | 0 | 0 | 0.023729 | 1.6925 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:17 | 0 | 0 | 26.3399 | 0.03913 | 0.97887 | 0 | 0 | 0 | 0.023728 | 1.6926 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:18 | 0 | 0 | 26.3408 | 0.036626 | 0.97886 | 0 | 0 | 0 | 0.023728 | 1.6926 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:19 | 0 | 0 | 26.3418 | 0.034584 | 0.97886 | 0 | 0 | 0 | 0.023727 | 1.6926 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:20 | 0 | 0 | 26.3429 | 0.032987 | 0.97886 | 0 | 0 | 0 | 0.023726 | 1.6927 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:21 | 0 | 0 | 26.344 | 0.032279 | 0.97886 | 0 | 0 | 0 | 0.023725 | 1.6927 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:22 | 0 | 0 | 26.3451 | 0.031646 | 0.97886 | 0 | 0 | 0 | 0.023725 | 1.6928 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:23 | 0 | 0 | 26.3461 | 0.029684 | 0.97885 | 0 | 0 | 0 | 0.023724 | 1.6928 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:24 | 0 | 0 | 26.3466 | 0.028644 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:25 | 0 | 0 | 26.3466 | 0.028069 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:26 | 0 | 0 | 26.3466 | 0.027912 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:27 | 0 | 0 | 26.3466 | 0.02784 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:28 | 0 | 0 | 26.3466 | 0.027193 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:29 | 0 | 0 | 26.3466 | 0.026561 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:30 | 0 | 0 | 26.3466 | 0.026137 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:31 | 0 | 0 | 26.3468 | 0.025278 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:32 | 0 | 0 | 26.3473 | 0.024479 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:33 | 0 | 0 | 26.3478 | 0.023872 | 0.97885 | 0 | 0 | 0 | 0.023723 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:34 | 0 | 0 | 26.3482 | 0.025266 | 0.97885 | 0 | 0 | 0 | 0.023722 | 1.6929 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:35 | 0 | 0 | 26.3487 | 0.022895 | 0.97885 | 0 | 0 | 0 | 0.023722 | 1.693 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:36 | 0 | 0 | 26.3491 | 0.020867 | 0.97885 | 0 | 0 | 0 | 0.023722 | 1.693 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:37 | 0 | 0 | 26.3496 | 0.01981 | 0.97885 | 0 | 0 | 0 | 0.023721 | 1.693 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:38 | 0 | 0 | 26.35 | 0.018893 | 0.97885 | 0 | 0 | 0 | 0.023721 | 1.693 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:39 | 0 | 0 | 26.3505 | 0.017984 | 0.97885 | 0 | 0 | 0 | 0.023721 | 1.693 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:40 | 0 | 0 | 26.3509 | 0.017057 | 0.97884 | 0 | 0 | 0 | 0.02372 | 1.6931 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:41 | 0 | 0 | 26.3513 | 0.016373 | 0.97884 | 0 | 0 | 0 | 0.02372 | 1.6931 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:42 | 0 | 0 | 26.3518 | 0.016052 | 0.97884 | 0 | 0 | 0 | 0.02372 | 1.6931 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:43 | 0 | 0 | 26.3523 | 0.015998 | 0.97884 | 0 | 0 | 0 | 0.023719 | 1.6931 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:44 | 0 | 0 | 26.353 | 0.016074 | 0.97884 | 0 | 0 | 0 | 0.023719 | 1.6931 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:45 | 0 | 0 | 26.3536 | 0.016217 | 0.97884 | 0 | 0 | 0 | 0.023718 | 1.6932 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:46 | 0 | 0 | 26.3543 | 0.016548 | 0.97884 | 0 | 0 | 0 | 0.023718 | 1.6932 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:47 | 0 | 0 | 26.3549 | 0.017048 | 0.97884 | 0 | 0 | 0 | 0.023718 | 1.6932 | 0 | 0 | #DIV/0! | #DIV/0!
2025-02-06 09:48 | 0.017374 | 0.01972 | 26.3557 | 0.018196 | 0.97883 | 0.019087 | 4.1315e-05 | 1703.7892 | 0.023717 | 1.6933 | 1.9676 | 2.2877 | 0.049191 | 0.0044364
2025-02-06 09:49 | 0.062931 | 0.07143 | 26.3565 | 0.019213 | 0.97883 | 0.069139 | 0.00014965 | 6171.532 | 0.023716 | 1.6933 | 5.952 | 6.9204 | 0.18085 | 0.01631
2025-02-06 09:50 | 0.098451 | 0.11175 | 26.3574 | 0.02019 | 0.97883 | 0.10816 | 0.00023412 | 9654.8956 | 0.023716 | 1.6933 | 8.7459 | 10.1691 | 0.29239 | 0.02637
2025-02-06 09:51 | 0.12972 | 0.14724 | 26.3583 | 0.022181 | 0.97883 | 0.14252 | 0.00030848 | 12721.8039 | 0.023715 | 1.6934 | 11.0874 | 12.892 | 0.41859 | 0.037752
2025-02-06 09:52 | 0.17567 | 0.19939 | 26.3591 | 0.024232 | 0.97883 | 0.19299 | 0.00041774 | 17227.5228 | 0.023715 | 1.6934 | 14.3903 | 16.7327 | 0.61133 | 0.055134
2025-02-06 09:53 | 0.20231 | 0.22963 | 26.3601 | 0.024782 | 0.97883 | 0.22226 | 0.00048109 | 19840.1545 | 0.023714 | 1.6935 | 16.2481 | 18.8935 | 0.71554 | 0.064533
2025-02-06 09:54 | 0.21891 | 0.24848 | 26.3612 | 0.025208 | 0.97882 | 0.2405 | 0.00052056 | 21468.384 | 0.023713 | 1.6935 | 17.3884 | 20.22 | 0.78476 | 0.070776
2025-02-06 09:55 | 0.22895 | 0.25987 | 26.3623 | 0.025901 | 0.97882 | 0.25153 | 0.00054443 | 22452.9556 | 0.023712 | 1.6936 | 18.072 | 21.0154 | 0.84161 | 0.075902
2025-02-06 09:56 | 0.24516 | 0.27828 | 26.3633 | 0.026459 | 0.97882 | 0.26934 | 0.000583 | 24043.3545 | 0.023712 | 1.6936 | 19.1674 | 22.2898 | 0.91775 | 0.08277
2025-02-06 09:57 | 0.26987 | 0.30633 | 26.3644 | 0.027164 | 0.97882 | 0.29649 | 0.00064175 | 26466.7748 | 0.023711 | 1.6937 | 20.8175 | 24.2093 | 1.0326 | 0.093125
2025-02-06 09:58 | 0.28763 | 0.32649 | 26.3652 | 0.02809 | 0.97882 | 0.316 | 0.00068399 | 28208.6318 | 0.02371 | 1.6937 | 21.9904 | 25.5738 | 1.1346 | 0.10233
2025-02-06 09:59 | 0.29342 | 0.33306 | 26.3659 | 0.029273 | 0.97881 | 0.32236 | 0.00069776 | 28776.6913 | 0.02371 | 1.6937 | 22.3706 | 26.0164 | 1.2051 | 0.10868
2025-02-06 10:00 | 0.30578 | 0.34709 | 26.3665 | 0.030171 | 0.97881 | 0.33594 | 0.00072714 | 29988.4466 | 0.023709 | 1.6938 | 23.1783 | 26.9561 | 1.2918 | 0.1165
2025-02-06 10:01 | 0.33628 | 0.38171 | 26.3671 | 0.031128 | 0.97881 | 0.36945 | 0.00079967 | 32979.8338 | 0.023709 | 1.6938 | 25.1533 | 29.2534 | 1.459 | 0.13158
2025-02-06 10:02 | 0.3355 | 0.38084 | 26.3678 | 0.032291 | 0.97881 | 0.3686 | 0.00079783 | 32904.2161 | 0.023708 | 1.6938 | 25.1036 | 29.196 | 1.5102 | 0.1362
2025-02-06 10:03 | 0.33049 | 0.37514 | 26.3672 | 0.033211 | 0.97881 | 0.36308 | 0.0007859 | 32411.8755 | 0.023709 | 1.6938 | 24.7803 | 28.8196 | 1.5311 | 0.13809
2025-02-06 10:04 | 0.33319 | 0.3782 | 26.3659 | 0.034164 | 0.97881 | 0.36605 | 0.00079232 | 32676.6976 | 0.02371 | 1.6937 | 24.9545 | 29.0213 | 1.5872 | 0.14315
2025-02-06 10:05 | 0.34245 | 0.38872 | 26.3646 | 0.035114 | 0.97882 | 0.37623 | 0.00081436 | 33585.2009 | 0.023711 | 1.6937 | 25.5501 | 29.7131 | 1.6744 | 0.15101
2025-02-06 10:06 | 0.32701 | 0.37119 | 26.3633 | 0.036153 | 0.97882 | 0.35927 | 0.00077763 | 32070.4251 | 0.023712 | 1.6936 | 24.556 | 28.5562 | 1.6499 | 0.1488
2025-02-06 10:07 | 0.31273 | 0.35497 | 26.362 | 0.036988 | 0.97882 | 0.34357 | 0.00074366 | 30669.2609 | 0.023713 | 1.6936 | 23.6307 | 27.4792 | 1.6177 | 0.14589
2025-02-06 10:08 | 0.30809 | 0.34971 | 26.3609 | 0.03769 | 0.97882 | 0.33848 | 0.00073265 | 30214.7134 | 0.023713 | 1.6935 | 23.3293 | 27.128 | 1.6251 | 0.14656
2025-02-06 10:09 | 0.32431 | 0.36811 | 26.3598 | 0.038095 | 0.97883 | 0.3563 | 0.00077121 | 31804.7765 | 0.023714 | 1.6935 | 24.3814 | 28.3508 | 1.7247 | 0.15554
2025-02-06 10:10 | 0.31659 | 0.35934 | 26.3587 | 0.038699 | 0.97883 | 0.34781 | 0.00075284 | 31047.3394 | 0.023715 | 1.6934 | 23.8813 | 27.7686 | 1.7122 | 0.15442
2025-02-06 10:11 | 0.3135 | 0.35584 | 26.3577 | 0.039195 | 0.97883 | 0.34442 | 0.0007455 | 30744.2599 | 0.023716 | 1.6934 | 23.6808 | 27.5347 | 1.718 | 0.15494
2025-02-06 10:12 | 0.33782 | 0.38344 | 26.3566 | 0.039642 | 0.97883 | 0.37114 | 0.00080334 | 33129.4009 | 0.023716 | 1.6933 | 25.2526 | 29.3615 | 1.8656 | 0.16825
2025-02-06 10:13 | 0.36446 | 0.41368 | 26.3565 | 0.039862 | 0.97883 | 0.40041 | 0.00086669 | 35741.8695 | 0.023716 | 1.6933 | 26.956 | 31.342 | 2.0163 | 0.18184
2025-02-06 10:14 | 0.38492 | 0.43691 | 26.3569 | 0.040058 | 0.97883 | 0.42289 | 0.00091535 | 37748.6527 | 0.023716 | 1.6933 | 28.2525 | 32.8498 | 2.1341 | 0.19247
2025-02-06 10:15 | 0.39651 | 0.45005 | 26.3574 | 0.040469 | 0.97883 | 0.43562 | 0.00094289 | 38884.6094 | 0.023716 | 1.6933 | 28.9821 | 33.6984 | 2.2176 | 0.2
2025-02-06 10:16 | 0.38415 | 0.43603 | 26.3578 | 0.04089 | 0.97883 | 0.42204 | 0.00091351 | 37673.1014 | 0.023716 | 1.6934 | 28.2037 | 32.7938 | 2.1744 | 0.1961
2025-02-06 10:17 | 0.37643 | 0.42727 | 26.3582 | 0.041046 | 0.97883 | 0.41356 | 0.00089515 | 36915.9355 | 0.023715 | 1.6934 | 27.7155 | 32.2264 | 2.141 | 0.19309
2025-02-06 10:18 | 0.37682 | 0.4277 | 26.3575 | 0.040972 | 0.97883 | 0.41398 | 0.00089607 | 36953.6642 | 0.023716 | 1.6933 | 27.7399 | 32.2543 | 2.1392 | 0.19293
2025-02-06 10:19 | 0.36987 | 0.41981 | 26.3562 | 0.04106 | 0.97883 | 0.40635 | 0.00087954 | 36271.8884 | 0.023717 | 1.6933 | 27.2994 | 31.7411 | 2.1061 | 0.18994
2025-02-06 10:20 | 0.37334 | 0.42375 | 26.3549 | 0.041295 | 0.97884 | 0.41017 | 0.00088781 | 36612.3914 | 0.023718 | 1.6932 | 27.5198 | 31.9964 | 2.137 | 0.19273
2025-02-06 10:21 | 0.3745 | 0.42507 | 26.3536 | 0.041327 | 0.97884 | 0.41144 | 0.00089056 | 36725.7188 | 0.023718 | 1.6932 | 27.5932 | 32.0808 | 2.1449 | 0.19344
2025-02-06 10:22 | 0.37604 | 0.42682 | 26.3524 | 0.041359 | 0.97884 | 0.41314 | 0.00089423 | 36876.9125 | 0.023719 | 1.6931 | 27.6911 | 32.1935 | 2.1548 | 0.19434
2025-02-06 10:23 | 0.37064 | 0.42068 | 26.3524 | 0.041481 | 0.97884 | 0.4072 | 0.00088138 | 36346.8491 | 0.023719 | 1.6931 | 27.3484 | 31.7952 | 2.1317 | 0.19225
2025-02-06 10:24 | 0.36871 | 0.41849 | 26.353 | 0.041611 | 0.97884 | 0.40508 | 0.00087679 | 36157.6688 | 0.023719 | 1.6931 | 27.2259 | 31.6532 | 2.1278 | 0.1919
2025-02-06 10:25 | 0.37759 | 0.42857 | 26.3536 | 0.041575 | 0.97884 | 0.41483 | 0.0008979 | 37028.6109 | 0.023718 | 1.6932 | 27.7888 | 32.3082 | 2.1746 | 0.19613
2025-02-06 10:26 | 0.38415 | 0.43602 | 26.3543 | 0.041602 | 0.97884 | 0.42204 | 0.00091351 | 37672.3885 | 0.023718 | 1.6932 | 28.2037 | 32.7911 | 2.212 | 0.19949
2025-02-06 10:27 | 0.38608 | 0.43822 | 26.3549 | 0.041753 | 0.97884 | 0.42416 | 0.0009181 | 37861.8287 | 0.023718 | 1.6932 | 28.3256 | 32.9332 | 2.2307 | 0.20118
2025-02-06 10:28 | 0.39033 | 0.44304 | 26.3554 | 0.041825 | 0.97884 | 0.42883 | 0.0009282 | 38278.4135 | 0.023717 | 1.6933 | 28.5933 | 33.2449 | 2.2579 | 0.20363
2025-02-06 10:29 | 0.36407 | 0.41324 | 26.3559 | 0.041801 | 0.97883 | 0.39999 | 0.00086577 | 35703.885 | 0.023717 | 1.6933 | 26.9314 | 31.3129 | 2.1122 | 0.19049
2025-02-06 10:30 | 0.35944 | 0.40798 | 26.3563 | 0.041791 | 0.97883 | 0.3949 | 0.00085475 | 35249.6221 | 0.023717 | 1.6933 | 26.6364 | 30.9703 | 2.0861 | 0.18814
2025-02-06 10:31 | 0.3606 | 0.4093 | 26.3567 | 0.041799 | 0.97883 | 0.39617 | 0.00085751 | 35363.2901 | 0.023716 | 1.6933 | 26.7102 | 31.0564 | 2.093 | 0.18876
2025-02-06 10:32 | 0.366 | 0.41543 | 26.3571 | 0.041898 | 0.97883 | 0.40211 | 0.00087036 | 35893.4438 | 0.023716 | 1.6933 | 27.0542 | 31.4566 | 2.1278 | 0.1919
2025-02-06 10:33 | 0.36987 | 0.41982 | 26.3573 | 0.04187 | 0.97883 | 0.40635 | 0.00087954 | 36272.0964 | 0.023716 | 1.6933 | 27.2994 | 31.7419 | 2.1477 | 0.1937
2025-02-06 10:34 | 0.37334 | 0.42376 | 26.3573 | 0.041992 | 0.97883 | 0.41017 | 0.00088781 | 36612.8573 | 0.023716 | 1.6933 | 27.5198 | 31.9982 | 2.1732 | 0.19599
2025-02-06 10:35 | 0.37257 | 0.42288 | 26.3573 | 0.042061 | 0.97883 | 0.40932 | 0.00088597 | 36537.1324 | 0.023716 | 1.6933 | 27.4709 | 31.9413 | 2.1725 | 0.19593
2025-02-06 10:36 | 0.40616 | 0.46101 | 26.3573 | 0.042013 | 0.97883 | 0.44622 | 0.00096584 | 39831.1535 | 0.023716 | 1.6933 | 29.5878 | 34.4027 | 2.3554 | 0.21243
2025-02-06 10:37 | 0.45326 | 0.51447 | 26.3573 | 0.042126 | 0.97883 | 0.49797 | 0.0010779 | 44450.3537 | 0.023716 | 1.6933 | 32.5157 | 37.8071 | 2.6209 | 0.23637
2025-02-06 10:38 | 0.45094 | 0.51184 | 26.3573 | 0.0421 | 0.97883 | 0.49542 | 0.0010723 | 44223.1801 | 0.023716 | 1.6933 | 32.3727 | 37.6408 | 2.6066 | 0.23508
2025-02-06 10:39 | 0.44978 | 0.51053 | 26.3573 | 0.042114 | 0.97883 | 0.49415 | 0.0010696 | 44109.5959 | 0.023716 | 1.6933 | 32.3012 | 37.5577 | 2.6011 | 0.23459
2025-02-06 10:40 | 0.46909 | 0.53244 | 26.3576 | 0.042133 | 0.97883 | 0.51536 | 0.0011155 | 46002.7832 | 0.023716 | 1.6934 | 33.4899 | 38.9401 | 2.7081 | 0.24424
2025-02-06 10:41 | 0.46561 | 0.5285 | 26.358 | 0.042235 | 0.97883 | 0.51154 | 0.0011072 | 45662.1276 | 0.023715 | 1.6934 | 33.2765 | 38.6923 | 2.6957 | 0.24311
2025-02-06 10:42 | 0.45905 | 0.52105 | 26.3584 | 0.042239 | 0.97883 | 0.50433 | 0.0010916 | 45018.5694 | 0.023715 | 1.6934 | 32.8727 | 38.2232 | 2.6599 | 0.23989
2025-02-06 10:43 | 0.47256 | 0.53639 | 26.3589 | 0.042331 | 0.97883 | 0.51918 | 0.0011238 | 46343.8662 | 0.023715 | 1.6934 | 33.7032 | 39.1892 | 2.7401 | 0.24712
2025-02-06 10:44 | 0.46098 | 0.52324 | 26.3593 | 0.042328 | 0.97883 | 0.50645 | 0.0010962 | 45208.0888 | 0.023714 | 1.6934 | 32.9915 | 38.3621 | 2.6762 | 0.24136
2025-02-06 10:45 | 0.44477 | 0.50484 | 26.359 | 0.042363 | 0.97883 | 0.48864 | 0.0010577 | 43617.7885 | 0.023715 | 1.6934 | 31.991 | 37.1985 | 2.5889 | 0.23349
2025-02-06 10:46 | 0.44283 | 0.50264 | 26.3584 | 0.042474 | 0.97883 | 0.48652 | 0.0010531 | 43428.3231 | 0.023715 | 1.6934 | 31.8716 | 37.059 | 2.585 | 0.23313
2025-02-06 10:47 | 0.43434 | 0.493 | 26.3577 | 0.042465 | 0.97883 | 0.47718 | 0.0010329 | 42595.1976 | 0.023716 | 1.6934 | 31.3451 | 36.4463 | 2.5373 | 0.22883
2025-02-06 10:48 | 0.43589 | 0.49475 | 26.3571 | 0.04242 | 0.97883 | 0.47888 | 0.0010365 | 42746.4978 | 0.023716 | 1.6933 | 31.4409 | 36.5572 | 2.5431 | 0.22936
2025-02-06 10:49 | 0.44168 | 0.50132 | 26.3564 | 0.042407 | 0.97883 | 0.48524 | 0.0010503 | 43314.2866 | 0.023716 | 1.6933 | 31.7999 | 36.974 | 2.5744 | 0.23218
2025-02-06 10:50 | 0.43087 | 0.48905 | 26.3567 | 0.042363 | 0.97883 | 0.47337 | 0.0010246 | 42254.1968 | 0.023716 | 1.6933 | 31.1293 | 36.1946 | 2.5119 | 0.22654
2025-02-06 10:51 | 0.43666 | 0.49563 | 26.3573 | 0.042268 | 0.97883 | 0.47973 | 0.0010384 | 42822.2791 | 0.023716 | 1.6933 | 31.4888 | 36.6131 | 2.5383 | 0.22892
2025-02-06 10:52 | 0.43897 | 0.49826 | 26.3579 | 0.042455 | 0.97883 | 0.48227 | 0.0010439 | 43049.6032 | 0.023715 | 1.6934 | 31.6324 | 36.7806 | 2.5624 | 0.2311
2025-02-06 10:53 | 0.44438 | 0.5044 | 26.3586 | 0.042576 | 0.97883 | 0.48821 | 0.0010567 | 43579.8284 | 0.023715 | 1.6934 | 31.9671 | 37.1704 | 2.5998 | 0.23447
2025-02-06 10:54 | 0.44592 | 0.50615 | 26.3592 | 0.042512 | 0.97883 | 0.48991 | 0.0010604 | 43731.4288 | 0.023715 | 1.6934 | 32.0626 | 37.282 | 2.6045 | 0.23489
2025-02-06 10:55 | 0.41967 | 0.47635 | 26.3594 | 0.042357 | 0.97883 | 0.46107 | 0.00099798 | 41156.8127 | 0.023714 | 1.6934 | 30.4324 | 35.3865 | 2.4498 | 0.22094
2025-02-06 10:56 | 0.42083 | 0.47767 | 26.3594 | 0.042353 | 0.97883 | 0.46234 | 0.0010007 | 41270.3996 | 0.023714 | 1.6934 | 30.5046 | 35.4705 | 2.456 | 0.2215
2025-02-06 10:57 | 0.42816 | 0.48599 | 26.3594 | 0.042369 | 0.97883 | 0.4704 | 0.0010182 | 41989.7921 | 0.023714 | 1.6934 | 30.9613 | 36.0016 | 2.4975 | 0.22525
2025-02-06 10:58 | 0.44631 | 0.50659 | 26.3594 | 0.042449 | 0.97883 | 0.49033 | 0.0010613 | 43769.3429 | 0.023714 | 1.6934 | 32.0865 | 37.3099 | 2.6027 | 0.23473
2025-02-06 10:59 | 0.46407 | 0.52675 | 26.3594 | 0.04257 | 0.97883 | 0.50984 | 0.0011036 | 45511.0285 | 0.023714 | 1.6934 | 33.1815 | 38.5832 | 2.7086 | 0.24428
2025-02-06 11:00 | 0.45866 | 0.52061 | 26.3594 | 0.042563 | 0.97883 | 0.50391 | 0.0010907 | 44980.948 | 0.023714 | 1.6934 | 32.8489 | 38.1964 | 2.6782 | 0.24154
2025-02-06 11:01 | 0.45094 | 0.51185 | 26.3595 | 0.042544 | 0.97883 | 0.49542 | 0.0010723 | 44223.6971 | 0.023714 | 1.6934 | 32.3727 | 37.6428 | 2.6343 | 0.23758
2025-02-06 11:02 | 0.43241 | 0.49082 | 26.36 | 0.042436 | 0.97883 | 0.47506 | 0.0010283 | 42406.4179 | 0.023714 | 1.6935 | 31.2253 | 36.309 | 2.5251 | 0.22773
2025-02-06 11:03 | 0.42353 | 0.48074 | 26.3609 | 0.042376 | 0.97882 | 0.46531 | 0.0010072 | 41535.7647 | 0.023713 | 1.6935 | 30.673 | 35.6675 | 2.4724 | 0.22298
2025-02-06 11:04 | 0.43975 | 0.49915 | 26.3617 | 0.042401 | 0.97882 | 0.48312 | 0.0010457 | 43126.2112 | 0.023713 | 1.6935 | 31.6803 | 36.8396 | 2.5637 | 0.23121
2025-02-06 11:05 | 0.47411 | 0.53815 | 26.3626 | 0.042423 | 0.97882 | 0.52087 | 0.0011274 | 46496.254 | 0.023712 | 1.6936 | 33.7979 | 39.3028 | 2.7548 | 0.24845
2025-02-06 11:06 | 0.47835 | 0.54297 | 26.3634 | 0.042566 | 0.97882 | 0.52554 | 0.0011375 | 46912.9688 | 0.023712 | 1.6936 | 34.0581 | 39.6062 | 2.7877 | 0.25141
2025-02-06 11:07 | 0.45789 | 0.51975 | 26.364 | 0.042646 | 0.97882 | 0.50306 | 0.0010889 | 44906.339 | 0.023711 | 1.6936 | 32.8013 | 38.1453 | 2.6795 | 0.24166
2025-02-06 11:08 | 0.45944 | 0.5215 | 26.3644 | 0.042725 | 0.97882 | 0.50475 | 0.0010925 | 45057.8983 | 0.023711 | 1.6937 | 32.8965 | 38.2563 | 2.6931 | 0.24289
2025-02-06 11:09 | 0.45596 | 0.51756 | 26.3649 | 0.042754 | 0.97882 | 0.50094 | 0.0010843 | 44717.2276 | 0.023711 | 1.6937 | 32.6824 | 38.0077 | 2.6756 | 0.24131
2025-02-06 11:10 | 0.46446 | 0.5272 | 26.3653 | 0.042859 | 0.97882 | 0.51027 | 0.0011045 | 45550.3374 | 0.02371 | 1.6937 | 33.2053 | 38.6162 | 2.7296 | 0.24617
2025-02-06 11:11 | 0.47256 | 0.53641 | 26.3657 | 0.042887 | 0.97881 | 0.51918 | 0.0011238 | 46345.59 | 0.02371 | 1.6937 | 33.7032 | 39.1956 | 2.7766 | 0.25042
2025-02-06 11:12 | 0.46098 | 0.52326 | 26.3664 | 0.042872 | 0.97881 | 0.50645 | 0.0010962 | 45209.8297 | 0.023709 | 1.6937 | 32.9915 | 38.3686 | 2.7111 | 0.24451
2025-02-06 11:13 | 0.44477 | 0.50486 | 26.3672 | 0.042709 | 0.97881 | 0.48864 | 0.0010577 | 43619.7167 | 0.023709 | 1.6938 | 31.991 | 37.2057 | 2.6107 | 0.23545
2025-02-06 11:14 | 0.45249 | 0.51362 | 26.3679 | 0.042789 | 0.97881 | 0.49712 | 0.001076 | 44377.1867 | 0.023708 | 1.6938 | 32.4681 | 37.7612 | 2.6587 | 0.23978
2025-02-06 11:15 | 0.4382 | 0.49741 | 26.3687 | 0.042713 | 0.97881 | 0.48143 | 0.001042 | 42976.3773 | 0.023708 | 1.6938 | 31.5846 | 36.7344 | 2.5744 | 0.23218
2025-02-06 11:16 | 0.41465 | 0.47068 | 26.3695 | 0.042954 | 0.97881 | 0.45555 | 0.00098604 | 40666.8026 | 0.023707 | 1.6939 | 30.1191 | 35.0306 | 2.4568 | 0.22157
2025-02-06 11:17 | 0.41156 | 0.46718 | 26.3702 | 0.043027 | 0.97881 | 0.45216 | 0.0009787 | 40364.0526 | 0.023707 | 1.6939 | 29.9261 | 34.8067 | 2.4437 | 0.22039
2025-02-06 11:18 | 0.3884 | 0.44088 | 26.371 | 0.043008 | 0.9788 | 0.42671 | 0.00092361 | 38092.3097 | 0.023706 | 1.694 | 28.4717 | 33.1157 | 2.3119 | 0.2085
2025-02-06 11:19 | 0.39959 | 0.45359 | 26.3712 | 0.043193 | 0.9788 | 0.43901 | 0.00095024 | 39190.4522 | 0.023706 | 1.694 | 29.1761 | 33.9352 | 2.3853 | 0.21513
2025-02-06 11:20 | 0.41735 | 0.47375 | 26.3712 | 0.043463 | 0.9788 | 0.45852 | 0.00099247 | 40932.2506 | 0.023706 | 1.694 | 30.2879 | 35.2284 | 2.5014 | 0.2256
2025-02-06 11:21 | 0.43473 | 0.49347 | 26.3712 | 0.043654 | 0.9788 | 0.47761 | 0.0010338 | 42636.1829 | 0.023706 | 1.694 | 31.3691 | 36.4859 | 2.6115 | 0.23553
2025-02-06 11:22 | 0.43241 | 0.49084 | 26.3712 | 0.043609 | 0.9788 | 0.47506 | 0.0010283 | 42408.9921 | 0.023706 | 1.694 | 31.2253 | 36.3187 | 2.5957 | 0.2341
2025-02-06 11:23 | 0.41967 | 0.47638 | 26.3712 | 0.043453 | 0.9788 | 0.46107 | 0.00099798 | 41159.4417 | 0.023706 | 1.694 | 30.4324 | 35.3964 | 2.514 | 0.22674
2025-02-06 11:24 | 0.42855 | 0.48646 | 26.3712 | 0.043463 | 0.9788 | 0.47082 | 0.0010191 | 42030.3404 | 0.023706 | 1.694 | 30.9854 | 36.0396 | 2.5651 | 0.23134
2025-02-06 11:25 | 0.44477 | 0.50487 | 26.3713 | 0.043587 | 0.9788 | 0.48864 | 0.0010577 | 43620.6844 | 0.023706 | 1.694 | 31.991 | 37.2093 | 2.6646 | 0.24032
2025-02-06 11:26 | 0.44863 | 0.50925 | 26.3722 | 0.043348 | 0.9788 | 0.49288 | 0.0010668 | 43999.5712 | 0.023705 | 1.694 | 32.2297 | 37.4878 | 2.672 | 0.24098
2025-02-06 11:27 | 0.45403 | 0.51539 | 26.3737 | 0.043301 | 0.9788 | 0.49882 | 0.0010797 | 44530.0434 | 0.023704 | 1.6941 | 32.5633 | 37.8772 | 2.6996 | 0.24347
2025-02-06 11:28 | 0.45789 | 0.51978 | 26.3752 | 0.04324 | 0.97879 | 0.50306 | 0.0010889 | 44909.0602 | 0.023703 | 1.6941 | 32.8013 | 38.1554 | 2.7177 | 0.24511
2025-02-06 11:29 | 0.45558 | 0.51716 | 26.3767 | 0.04323 | 0.97879 | 0.50051 | 0.0010834 | 44682.2231 | 0.023702 | 1.6942 | 32.6586 | 37.9907 | 2.7041 | 0.24388
2025-02-06 11:30 | 0.45828 | 0.52023 | 26.3782 | 0.043357 | 0.97879 | 0.50348 | 0.0010898 | 44947.648 | 0.023701 | 1.6943 | 32.8251 | 38.1858 | 2.7275 | 0.24598
2025-02-06 11:31 | 0.44245 | 0.50226 | 26.3794 | 0.043272 | 0.97879 | 0.48609 | 0.0010521 | 43395.4063 | 0.0237 | 1.6943 | 31.8477 | 37.0497 | 2.633 | 0.23746
2025-02-06 11:32 | 0.39187 | 0.44485 | 26.3805 | 0.0433 | 0.97878 | 0.43053 | 0.00093187 | 38435.0714 | 0.023699 | 1.6944 | 28.6906 | 33.3778 | 2.348 | 0.21176
2025-02-06 11:33 | 0.40268 | 0.45712 | 26.3816 | 0.043435 | 0.97878 | 0.4424 | 0.00095758 | 39495.5791 | 0.023699 | 1.6944 | 29.37 | 34.1691 | 2.4171 | 0.21799
2025-02-06 11:34 | 0.41581 | 0.47203 | 26.3826 | 0.043644 | 0.97878 | 0.45682 | 0.0009888 | 40783.3054 | 0.023698 | 1.6945 | 30.1915 | 35.1257 | 2.5038 | 0.22582
2025-02-06 11:35 | 0.41542 | 0.47159 | 26.3837 | 0.043772 | 0.97878 | 0.4564 | 0.00098788 | 40745.6704 | 0.023697 | 1.6945 | 30.1674 | 35.0985 | 2.5091 | 0.22629
2025-02-06 11:36 | 0.42816 | 0.48606 | 26.3833 | 0.043827 | 0.97878 | 0.4704 | 0.0010182 | 41995.2209 | 0.023697 | 1.6945 | 30.9613 | 36.022 | 2.5853 | 0.23316
2025-02-06 11:37 | 0.43087 | 0.48912 | 26.382 | 0.043801 | 0.97878 | 0.47337 | 0.0010246 | 42260.0009 | 0.023698 | 1.6944 | 31.1293 | 36.2163 | 2.5991 | 0.23441
2025-02-06 11:38 | 0.43087 | 0.48912 | 26.3807 | 0.043719 | 0.97878 | 0.47337 | 0.0010246 | 42259.7063 | 0.023699 | 1.6944 | 31.1293 | 36.2152 | 2.5941 | 0.23396
2025-02-06 11:39 | 0.41542 | 0.47158 | 26.3795 | 0.043664 | 0.97879 | 0.4564 | 0.00098788 | 40744.7371 | 0.0237 | 1.6943 | 30.1674 | 35.095 | 2.5026 | 0.2257
2025-02-06 11:40 | 0.41697 | 0.47333 | 26.3782 | 0.043686 | 0.97879 | 0.4581 | 0.00099155 | 40895.921 | 0.023701 | 1.6943 | 30.2638 | 35.2061 | 2.5126 | 0.2266
2025-02-06 11:41 | 0.43975 | 0.49919 | 26.3781 | 0.043694 | 0.97879 | 0.48312 | 0.0010457 | 43130.0245 | 0.023701 | 1.6943 | 31.6803 | 36.8539 | 2.6431 | 0.23838
2025-02-06 11:42 | 0.41079 | 0.46632 | 26.3787 | 0.04363 | 0.97879 | 0.45131 | 0.00097686 | 40290.1717 | 0.023701 | 1.6943 | 29.8778 | 34.7575 | 2.4741 | 0.22313
2025-02-06 11:43 | 0.40461 | 0.45931 | 26.3794 | 0.043675 | 0.97879 | 0.44452 | 0.00096217 | 39684.4426 | 0.0237 | 1.6943 | 29.491 | 34.3081 | 2.4413 | 0.22017
2025-02-06 11:44 | 0.40307 | 0.45756 | 26.38 | 0.043692 | 0.97879 | 0.44283 | 0.0009585 | 39533.114 | 0.0237 | 1.6944 | 29.3942 | 34.196 | 2.4334 | 0.21947
2025-02-06 11:45 | 0.38029 | 0.4317 | 26.3806 | 0.043584 | 0.97878 | 0.4178 | 0.00090433 | 37299.0939 | 0.023699 | 1.6944 | 27.9598 | 32.5278 | 2.297 | 0.20716
2025-02-06 11:46 | 0.38994 | 0.44266 | 26.3816 | 0.043443 | 0.97878 | 0.42841 | 0.00092728 | 38245.9594 | 0.023699 | 1.6944 | 28.569 | 33.2372 | 2.3448 | 0.21147
2025-02-06 11:47 | 0.36909 | 0.419 | 26.3826 | 0.04335 | 0.97878 | 0.4055 | 0.00087771 | 36201.3363 | 0.023698 | 1.6945 | 27.2504 | 31.7039 | 2.2209 | 0.20029
2025-02-06 11:48 | 0.35712 | 0.40541 | 26.3837 | 0.043505 | 0.97878 | 0.39235 | 0.00084924 | 35027.6466 | 0.023697 | 1.6945 | 26.4887 | 30.8186 | 2.1601 | 0.19482
2025-02-06 11:49 | 0.35712 | 0.40541 | 26.3848 | 0.043691 | 0.97878 | 0.39235 | 0.00084924 | 35027.8504 | 0.023696 | 1.6946 | 26.4887 | 30.8194 | 2.1694 | 0.19565
2025-02-06 11:50 | 0.33049 | 0.37518 | 26.3858 | 0.043602 | 0.97877 | 0.36308 | 0.0007859 | 32415.1501 | 0.023696 | 1.6946 | 24.7803 | 28.8324 | 2.0112 | 0.18139
2025-02-06 11:51 | 0.32547 | 0.36948 | 26.3865 | 0.043561 | 0.97877 | 0.35757 | 0.00077396 | 31922.9806 | 0.023695 | 1.6946 | 24.4563 | 28.4558 | 1.9804 | 0.1786
2025-02-06 11:52 | 0.32778 | 0.37211 | 26.387 | 0.043669 | 0.97877 | 0.36011 | 0.00077947 | 32150.2649 | 0.023695 | 1.6947 | 24.6059 | 28.6302 | 1.9987 | 0.18026
2025-02-06 11:53 | 0.31581 | 0.35852 | 26.3874 | 0.04381 | 0.97877 | 0.34697 | 0.00075101 | 30976.417 | 0.023695 | 1.6947 | 23.8312 | 27.7291 | 1.9355 | 0.17456
2025-02-06 11:54 | 0.29883 | 0.33924 | 26.3878 | 0.043907 | 0.97877 | 0.3283 | 0.00071061 | 29310.2714 | 0.023694 | 1.6947 | 22.7246 | 26.4417 | 1.8403 | 0.16598
2025-02-06 11:55 | 0.27489 | 0.31207 | 26.3882 | 0.043839 | 0.97877 | 0.302 | 0.00065369 | 26962.4834 | 0.023694 | 1.6947 | 21.1501 | 24.6099 | 1.6971 | 0.15306
2025-02-06 11:56 | 0.27566 | 0.31294 | 26.3891 | 0.043986 | 0.97877 | 0.30285 | 0.00065553 | 27038.3416 | 0.023693 | 1.6948 | 21.2011 | 24.6698 | 1.7074 | 0.15399
2025-02-06 11:57 | 0.27257 | 0.30944 | 26.3901 | 0.044259 | 0.97876 | 0.29946 | 0.00064818 | 26735.5474 | 0.023693 | 1.6948 | 20.9967 | 24.4326 | 1.6997 | 0.15329
2025-02-06 11:58 | 0.2552 | 0.28972 | 26.3912 | 0.044502 | 0.97876 | 0.28037 | 0.00060687 | 25031.5857 | 0.023692 | 1.6949 | 19.8405 | 23.0877 | 1.6051 | 0.14476
2025-02-06 11:59 | 0.25327 | 0.28753 | 26.3923 | 0.044618 | 0.97876 | 0.27825 | 0.00060228 | 24842.3834 | 0.023691 | 1.6949 | 19.7113 | 22.938 | 1.5977 | 0.1441
2025-02-06 12:00 | 0.23937 | 0.27175 | 26.3934 | 0.044476 | 0.97876 | 0.26298 | 0.00056922 | 23479.2176 | 0.02369 | 1.695 | 18.7774 | 21.8518 | 1.5093 | 0.13612
2025-02-06 12:01 | 0.25597 | 0.2906 | 26.394 | 0.044504 | 0.97876 | 0.28122 | 0.0006087 | 25107.707 | 0.02369 | 1.695 | 19.8921 | 23.1493 | 1.61 | 0.1452
2025-02-06 12:02 | 0.25636 | 0.29104 | 26.3945 | 0.044846 | 0.97876 | 0.28164 | 0.00060962 | 25145.6353 | 0.02369 | 1.695 | 19.9179 | 23.1796 | 1.6247 | 0.14652
2025-02-06 12:03 | 0.24362 | 0.27657 | 26.3949 | 0.045156 | 0.97875 | 0.26765 | 0.00057932 | 23895.9833 | 0.023689 | 1.695 | 19.0636 | 22.1856 | 1.5583 | 0.14054
2025-02-06 12:04 | 0.23319 | 0.26474 | 26.3953 | 0.045262 | 0.97875 | 0.25619 | 0.00055453 | 22873.5456 | 0.023689 | 1.695 | 18.3599 | 21.3669 | 1.4982 | 0.13512
2025-02-06 12:05 | 0.22045 | 0.25028 | 26.3958 | 0.045314 | 0.97875 | 0.2422 | 0.00052424 | 21623.8834 | 0.023689 | 1.6951 | 17.4939 | 20.3593 | 1.4216 | 0.12821
2025-02-06 12:06 | 0.22354 | 0.25378 | 26.397 | 0.045423 | 0.97875 | 0.24559 | 0.00053158 | 21926.9871 | 0.023688 | 1.6951 | 17.7044 | 20.6049 | 1.4442 | 0.13025
2025-02-06 12:07 | 0.23165 | 0.26299 | 26.3987 | 0.045397 | 0.97875 | 0.2545 | 0.00055086 | 22722.4754 | 0.023687 | 1.6952 | 18.2553 | 21.2469 | 1.4933 | 0.13468
2025-02-06 12:08 | 0.23165 | 0.26299 | 26.4003 | 0.045475 | 0.97874 | 0.2545 | 0.00055086 | 22722.6839 | 0.023685 | 1.6953 | 18.2553 | 21.2477 | 1.496 | 0.13492
2025-02-06 12:09 | 0.23744 | 0.26957 | 26.402 | 0.045517 | 0.97874 | 0.26086 | 0.00056463 | 23290.9651 | 0.023684 | 1.6953 | 18.6471 | 21.7046 | 1.5331 | 0.13827
2025-02-06 12:10 | 0.24748 | 0.28097 | 26.4037 | 0.045712 | 0.97874 | 0.27189 | 0.0005885 | 24275.8468 | 0.023683 | 1.6954 | 19.3231 | 22.4924 | 1.6017 | 0.14446
2025-02-06 12:11 | 0.25404 | 0.28842 | 26.405 | 0.045771 | 0.97873 | 0.2791 | 0.00060411 | 24919.834 | 0.023682 | 1.6955 | 19.763 | 23.0051 | 1.6444 | 0.1483
2025-02-06 12:12 | 0.26717 | 0.30333 | 26.4058 | 0.045986 | 0.97873 | 0.29352 | 0.00063533 | 26207.6065 | 0.023682 | 1.6955 | 20.6381 | 24.0242 | 1.7334 | 0.15633
2025-02-06 12:13 | 0.27412 | 0.31122 | 26.4067 | 0.046103 | 0.97873 | 0.30116 | 0.00065185 | 26889.4329 | 0.023681 | 1.6956 | 21.099 | 24.5612 | 1.7809 | 0.16062
2025-02-06 12:14 | 0.26871 | 0.30508 | 26.4075 | 0.045754 | 0.97873 | 0.29522 | 0.000639 | 26359.3418 | 0.02368 | 1.6956 | 20.7407 | 24.1446 | 1.7342 | 0.15641
2025-02-06 12:15 | 0.28223 | 0.32043 | 26.4084 | 0.045468 | 0.97873 | 0.31006 | 0.00067113 | 27685.0117 | 0.02368 | 1.6956 | 21.6345 | 25.1857 | 1.8059 | 0.16287
2025-02-06 12:16 | 0.30886 | 0.35068 | 26.4094 | 0.045338 | 0.97873 | 0.33933 | 0.00073448 | 30298.3943 | 0.023679 | 1.6957 | 23.3795 | 27.2178 | 1.9623 | 0.17697
2025-02-06 12:17 | 0.32547 | 0.36953 | 26.4105 | 0.045048 | 0.97872 | 0.35757 | 0.00077396 | 31927.1183 | 0.023678 | 1.6957 | 24.4563 | 28.472 | 2.0494 | 0.18483
2025-02-06 12:18 | 0.3413 | 0.3875 | 26.4115 | 0.044898 | 0.97872 | 0.37496 | 0.0008116 | 33480.114 | 0.023678 | 1.6958 | 25.4758 | 29.6597 | 2.137 | 0.19273
2025-02-06 12:19 | 0.37334 | 0.42389 | 26.4126 | 0.044714 | 0.97872 | 0.41017 | 0.00088781 | 36623.8218 | 0.023677 | 1.6958 | 27.5198 | 32.0402 | 2.3178 | 0.20903
2025-02-06 12:20 | 0.405 | 0.45983 | 26.4137 | 0.044441 | 0.97872 | 0.44495 | 0.00096309 | 39729.6927 | 0.023676 | 1.6959 | 29.5152 | 34.3642 | 2.4888 | 0.22446
2025-02-06 12:21 | 0.40577 | 0.46071 | 26.4145 | 0.044128 | 0.97872 | 0.4458 | 0.00096493 | 39805.6212 | 0.023675 | 1.6959 | 29.5636 | 34.4212 | 2.4758 | 0.22329
2025-02-06 12:22 | 0.39921 | 0.45326 | 26.4152 | 0.044 | 0.97871 | 0.43858 | 0.00094932 | 39161.8984 | 0.023675 | 1.6959 | 29.1519 | 33.9424 | 2.4308 | 0.21923
2025-02-06 12:23 | 0.39959 | 0.4537 | 26.4158 | 0.044045 | 0.97871 | 0.43901 | 0.00095024 | 39199.9102 | 0.023675 | 1.696 | 29.1761 | 33.9711 | 2.4355 | 0.21965
2025-02-06 12:24 | 0.39419 | 0.44757 | 26.4164 | 0.043877 | 0.97871 | 0.43307 | 0.00093738 | 38669.8056 | 0.023674 | 1.696 | 28.8364 | 33.5761 | 2.3951 | 0.21601
2025-02-06 12:25 | 0.37141 | 0.42171 | 26.4171 | 0.043791 | 0.97871 | 0.40805 | 0.00088321 | 36435.3407 | 0.023674 | 1.696 | 27.3974 | 31.9011 | 2.2591 | 0.20374
2025-02-06 12:26 | 0.36407 | 0.41338 | 26.4183 | 0.043719 | 0.97871 | 0.39999 | 0.00086577 | 35715.962 | 0.023673 | 1.6961 | 26.9314 | 31.3594 | 2.2131 | 0.19959
2025-02-06 12:27 | 0.36137 | 0.41031 | 26.42 | 0.043497 | 0.9787 | 0.39702 | 0.00085934 | 35451.1682 | 0.023672 | 1.6962 | 26.7594 | 31.1603 | 2.1864 | 0.19719
2025-02-06 12:28 | 0.3633 | 0.41251 | 26.4217 | 0.04344 | 0.9787 | 0.39914 | 0.00086393 | 35640.8754 | 0.02367 | 1.6962 | 26.8823 | 31.3047 | 2.1947 | 0.19794
2025-02-06 12:29 | 0.35635 | 0.40462 | 26.4235 | 0.043293 | 0.9787 | 0.3915 | 0.00084741 | 34959.4408 | 0.023669 | 1.6963 | 26.4394 | 30.7903 | 2.1477 | 0.19369
2025-02-06 12:30 | 0.3467 | 0.39367 | 26.4252 | 0.043279 | 0.97869 | 0.3809 | 0.00082446 | 34012.8597 | 0.023668 | 1.6964 | 25.8224 | 30.0729 | 2.0918 | 0.18865
2025-02-06 12:31 | 0.35404 | 0.402 | 26.4255 | 0.043055 | 0.97869 | 0.38896 | 0.0008419 | 34732.5735 | 0.023668 | 1.6964 | 26.2916 | 30.6196 | 2.1228 | 0.19145
2025-02-06 12:32 | 0.35674 | 0.40506 | 26.4248 | 0.043172 | 0.97869 | 0.39193 | 0.00084833 | 34997.5621 | 0.023668 | 1.6964 | 26.4641 | 30.8199 | 2.1439 | 0.19335
2025-02-06 12:33 | 0.35481 | 0.40287 | 26.424 | 0.043274 | 0.9787 | 0.38981 | 0.00084374 | 34808.0369 | 0.023669 | 1.6963 | 26.3409 | 30.6759 | 2.1379 | 0.19281
2025-02-06 12:34 | 0.35211 | 0.3998 | 26.4232 | 0.043394 | 0.9787 | 0.38684 | 0.00083731 | 34542.7618 | 0.023669 | 1.6963 | 26.1682 | 30.4743 | 2.1283 | 0.19194
2025-02-06 12:35 | 0.34825 | 0.39542 | 26.4225 | 0.043177 | 0.9787 | 0.3826 | 0.00082813 | 34163.8619 | 0.02367 | 1.6963 | 25.9213 | 30.1861 | 2.0955 | 0.18899
2025-02-06 12:36 | 0.34477 | 0.39147 | 26.4217 | 0.042738 | 0.9787 | 0.37878 | 0.00081987 | 33822.8406 | 0.02367 | 1.6962 | 25.6987 | 29.9264 | 2.0545 | 0.18529
2025-02-06 12:37 | 0.33782 | 0.38358 | 26.4209 | 0.042537 | 0.9787 | 0.37114 | 0.00080334 | 33140.9434 | 0.023671 | 1.6962 | 25.2526 | 29.4063 | 2.0056 | 0.18088
2025-02-06 12:38 | 0.36871 | 0.41865 | 26.421 | 0.042607 | 0.9787 | 0.40508 | 0.00087679 | 36170.9879 | 0.023671 | 1.6962 | 27.2259 | 31.7043 | 2.1831 | 0.19688
2025-02-06 12:39 | 0.40384 | 0.45854 | 26.4218 | 0.042656 | 0.9787 | 0.44367 | 0.00096034 | 39617.8123 | 0.02367 | 1.6962 | 29.4426 | 34.2863 | 2.383 | 0.21491
2025-02-06 12:40 | 0.37566 | 0.42654 | 26.4225 | 0.042856 | 0.9787 | 0.41271 | 0.00089331 | 36853.05 | 0.02367 | 1.6963 | 27.6666 | 32.2187 | 2.2352 | 0.20159
2025-02-06 12:41 | 0.3718 | 0.42216 | 26.4233 | 0.043075 | 0.9787 | 0.40847 | 0.00088413 | 36474.444 | 0.023669 | 1.6963 | 27.4219 | 31.9343 | 2.2247 | 0.20064
2025-02-06 12:42 | 0.35906 | 0.40769 | 26.4241 | 0.043266 | 0.9787 | 0.39447 | 0.00085384 | 35224.6889 | 0.023669 | 1.6963 | 26.6118 | 30.9914 | 2.1618 | 0.19497
2025-02-06 12:43 | 0.37141 | 0.42172 | 26.4248 | 0.043452 | 0.97869 | 0.40805 | 0.00088321 | 36436.873 | 0.023668 | 1.6964 | 27.3974 | 31.9069 | 2.2421 | 0.20221
2025-02-06 12:44 | 0.36214 | 0.4112 | 26.4256 | 0.043511 | 0.97869 | 0.39787 | 0.00086118 | 35527.9913 | 0.023668 | 1.6964 | 26.8085 | 31.2217 | 2.1919 | 0.19768
2025-02-06 12:45 | 0.36253 | 0.41164 | 26.4245 | 0.043598 | 0.97869 | 0.39829 | 0.0008621 | 35565.6607 | 0.023668 | 1.6964 | 26.8331 | 31.2495 | 2.1985 | 0.19827
2025-02-06 12:46 | 0.39187 | 0.44495 | 26.422 | 0.043346 | 0.9787 | 0.43053 | 0.00093187 | 38443.7094 | 0.02367 | 1.6962 | 28.6906 | 33.4107 | 2.3533 | 0.21224
2025-02-06 12:47 | 0.41388 | 0.46993 | 26.4194 | 0.043212 | 0.97871 | 0.4547 | 0.00098421 | 40602.0507 | 0.023672 | 1.6961 | 30.0709 | 35.0159 | 2.4707 | 0.22283
2025-02-06 12:48 | 0.39921 | 0.45327 | 26.4168 | 0.042946 | 0.97871 | 0.43858 | 0.00094932 | 39162.2514 | 0.023674 | 1.696 | 29.1519 | 33.9437 | 2.3727 | 0.21399
2025-02-06 12:49 | 0.40345 | 0.45808 | 26.4142 | 0.042711 | 0.97872 | 0.44325 | 0.00095942 | 39578.3194 | 0.023676 | 1.6959 | 29.4184 | 34.2519 | 2.3833 | 0.21495
2025-02-06 12:50 | 0.40732 | 0.46247 | 26.4141 | 0.042821 | 0.97872 | 0.44749 | 0.0009686 | 39957.0384 | 0.023676 | 1.6959 | 29.6603 | 34.5336 | 2.4112 | 0.21746
2025-02-06 12:51 | 0.38994 | 0.44274 | 26.4161 | 0.042983 | 0.97871 | 0.42841 | 0.00092728 | 38253.1103 | 0.023674 | 1.696 | 28.569 | 33.2645 | 2.3223 | 0.20944
2025-02-06 12:52 | 0.40384 | 0.45853 | 26.418 | 0.042868 | 0.97871 | 0.44367 | 0.00096034 | 39617.0025 | 0.023673 | 1.6961 | 29.4426 | 34.2832 | 2.3945 | 0.21595
2025-02-06 12:53 | 0.42894 | 0.48703 | 26.4199 | 0.042964 | 0.9787 | 0.47125 | 0.00102 | 42079.3016 | 0.023672 | 1.6961 | 31.0094 | 36.1092 | 2.5414 | 0.2292
2025-02-06 12:54 | 0.43396 | 0.49273 | 26.4219 | 0.043128 | 0.9787 | 0.47676 | 0.0010319 | 42572.1241 | 0.02367 | 1.6962 | 31.3212 | 36.4739 | 2.5795 | 0.23264
2025-02-06 12:55 | 0.45056 | 0.51158 | 26.4221 | 0.043066 | 0.9787 | 0.495 | 0.0010714 | 44200.8399 | 0.02367 | 1.6962 | 32.3489 | 37.671 | 2.6693 | 0.24073
2025-02-06 12:56 | 0.44515 | 0.50544 | 26.4211 | 0.042866 | 0.9787 | 0.48906 | 0.0010586 | 43670.3258 | 0.023671 | 1.6962 | 32.0149 | 37.2811 | 2.6265 | 0.23688
2025-02-06 12:57 | 0.43975 | 0.4993 | 26.42 | 0.042933 | 0.9787 | 0.48312 | 0.0010457 | 43139.8197 | 0.023672 | 1.6962 | 31.6803 | 36.8905 | 2.6002 | 0.23451
2025-02-06 12:58 | 0.45866 | 0.52078 | 26.4189 | 0.043152 | 0.97871 | 0.50391 | 0.0010907 | 44995.4412 | 0.023672 | 1.6961 | 32.8489 | 38.2504 | 2.7199 | 0.2453
2025-02-06 12:59 | 0.45673 | 0.51859 | 26.4179 | 0.043221 | 0.97871 | 0.50179 | 0.0010861 | 44805.8071 | 0.023673 | 1.6961 | 32.73 | 38.1109 | 2.7133 | 0.24471
2025-02-06 13:00 | 0.45017 | 0.51113 | 26.4167 | 0.043221 | 0.97871 | 0.49457 | 0.0010705 | 44161.6536 | 0.023674 | 1.696 | 32.3251 | 37.6384 | 2.6763 | 0.24137
2025-02-06 13:01 | 0.44863 | 0.50937 | 26.4154 | 0.04322 | 0.97871 | 0.49288 | 0.0010668 | 44009.8488 | 0.023675 | 1.6959 | 32.2297 | 37.5262 | 2.6674 | 0.24056
2025-02-06 13:02 | 0.42894 | 0.48701 | 26.4141 | 0.043189 | 0.97872 | 0.47125 | 0.00102 | 42077.969 | 0.023676 | 1.6959 | 31.0094 | 36.1042 | 2.5542 | 0.23036
2025-02-06 13:03 | 0.37643 | 0.42739 | 26.4128 | 0.043208 | 0.97872 | 0.41356 | 0.00089515 | 36926.8524 | 0.023677 | 1.6958 | 27.7155 | 32.2682 | 2.2573 | 0.20358
2025-02-06 13:04 | 0.39651 | 0.45019 | 26.4115 | 0.043255 | 0.97872 | 0.43562 | 0.00094289 | 38896.0124 | 0.023678 | 1.6958 | 28.9821 | 33.7418 | 2.374 | 0.21411
2025-02-06 13:05 | 0.46059 | 0.52295 | 26.4119 | 0.043268 | 0.97872 | 0.50603 | 0.0010953 | 45183.0912 | 0.023677 | 1.6958 | 32.9678 | 38.3824 | 2.7376 | 0.24689
2025-02-06 13:06 | 0.46137 | 0.52383 | 26.4136 | 0.04324 | 0.97872 | 0.50688 | 0.0010971 | 45259.2594 | 0.023676 | 1.6959 | 33.0153 | 38.4392 | 2.7403 | 0.24714
2025-02-06 13:07 | 0.44515 | 0.50543 | 26.4153 | 0.043356 | 0.97871 | 0.48906 | 0.0010586 | 43668.9628 | 0.023675 | 1.6959 | 32.0149 | 37.276 | 2.6561 | 0.23955
2025-02-06 13:08 | 0.4494 | 0.51025 | 26.417 | 0.043414 | 0.97871 | 0.49373 | 0.0010687 | 44085.9893 | 0.023674 | 1.696 | 32.2774 | 37.5832 | 2.6839 | 0.24205
2025-02-06 13:09 | 0.46832 | 0.53174 | 26.4187 | 0.043483 | 0.97871 | 0.51451 | 0.0011137 | 45942.27 | 0.023672 | 1.6961 | 33.4425 | 38.9414 | 2.7955 | 0.25212
2025-02-06 13:10 | 0.4494 | 0.51026 | 26.4203 | 0.043607 | 0.9787 | 0.49373 | 0.0010687 | 44086.7815 | 0.023671 | 1.6962 | 32.2774 | 37.5861 | 2.6961 | 0.24315
2025-02-06 13:11 | 0.44168 | 0.5015 | 26.4218 | 0.043612 | 0.9787 | 0.48524 | 0.0010503 | 43329.63 | 0.02367 | 1.6962 | 31.7999 | 37.0314 | 2.6525 | 0.23922
2025-02-06 13:12 | 0.43087 | 0.48923 | 26.4233 | 0.043476 | 0.9787 | 0.47337 | 0.0010246 | 42269.4595 | 0.023669 | 1.6963 | 31.1293 | 36.2518 | 2.5829 | 0.23294
2025-02-06 13:13 | 0.43859 | 0.498 | 26.4248 | 0.043648 | 0.97869 | 0.48185 | 0.001043 | 43027.3262 | 0.023668 | 1.6964 | 31.6085 | 36.8112 | 2.6373 | 0.23785
2025-02-06 13:14 | 0.46098 | 0.52343 | 26.4264 | 0.043752 | 0.97869 | 0.50645 | 0.0010962 | 45224.5116 | 0.023667 | 1.6964 | 32.9915 | 38.4232 | 2.7715 | 0.24996
2025-02-06 13:15 | 0.48106 | 0.54623 | 26.4273 | 0.043913 | 0.97869 | 0.52851 | 0.001144 | 47194.3265 | 0.023666 | 1.6965 | 34.2235 | 39.8589 | 2.8966 | 0.26124
2025-02-06 13:16 | 0.47874 | 0.5436 | 26.4277 | 0.043953 | 0.97869 | 0.52596 | 0.0011384 | 46967.1838 | 0.023666 | 1.6965 | 34.0817 | 39.6942 | 2.886 | 0.26028
2025-02-06 13:17 | 0.466 | 0.52914 | 26.4282 | 0.044004 | 0.97869 | 0.51197 | 0.0011081 | 45717.3649 | 0.023666 | 1.6965 | 33.3002 | 38.7844 | 2.8165 | 0.25401
2025-02-06 13:18 | 0.46523 | 0.52826 | 26.4287 | 0.044037 | 0.97869 | 0.51112 | 0.0011063 | 45641.7247 | 0.023665 | 1.6965 | 33.2528 | 38.7296 | 2.8142 | 0.2538
2025-02-06 13:19 | 0.46793 | 0.53133 | 26.4291 | 0.044171 | 0.97869 | 0.51409 | 0.0011127 | 45906.9788 | 0.023665 | 1.6966 | 33.4188 | 38.9234 | 2.8383 | 0.25598
2025-02-06 13:20 | 0.45249 | 0.5138 | 26.4296 | 0.044317 | 0.97868 | 0.49712 | 0.001076 | 44392.0073 | 0.023665 | 1.6966 | 32.4681 | 37.8165 | 2.7585 | 0.24878
2025-02-06 13:21 | 0.43087 | 0.48925 | 26.43 | 0.044168 | 0.97868 | 0.47337 | 0.0010246 | 42270.9924 | 0.023664 | 1.6966 | 31.1293 | 36.2576 | 2.6245 | 0.2367
2025-02-06 13:22 | 0.44245 | 0.5024 | 26.4305 | 0.044217 | 0.97868 | 0.48609 | 0.0010521 | 43407.4125 | 0.023664 | 1.6966 | 31.8477 | 37.0946 | 2.6944 | 0.243
2025-02-06 13:23 | 0.44708 | 0.50766 | 26.4309 | 0.044344 | 0.97868 | 0.49118 | 0.0010632 | 43862.042 | 0.023664 | 1.6966 | 32.1342 | 37.4288 | 2.729 | 0.24612
2025-02-06 13:24 | 0.43666 | 0.49583 | 26.4313 | 0.044537 | 0.97868 | 0.47973 | 0.0010384 | 42839.4534 | 0.023664 | 1.6967 | 31.4888 | 36.6774 | 2.6803 | 0.24173
2025-02-06 13:25 | 0.4467 | 0.50723 | 26.4318 | 0.044676 | 0.97868 | 0.49076 | 0.0010622 | 43824.3697 | 0.023663 | 1.6967 | 32.1104 | 37.4018 | 2.7473 | 0.24777
2025-02-06 13:26 | 0.43589 | 0.49495 | 26.4322 | 0.044836 | 0.97868 | 0.47888 | 0.0010365 | 42763.8956 | 0.023663 | 1.6967 | 31.4409 | 36.6224 | 2.6938 | 0.24295
2025-02-06 13:27 | 0.42276 | 0.48005 | 26.432 | 0.044926 | 0.97868 | 0.46446 | 0.0010053 | 41476.0193 | 0.023663 | 1.6967 | 30.6249 | 35.6718 | 2.622 | 0.23647
2025-02-06 13:28 | 0.43859 | 0.49802 | 26.4314 | 0.045011 | 0.97868 | 0.48185 | 0.001043 | 43028.8523 | 0.023664 | 1.6967 | 31.6085 | 36.8169 | 2.7202 | 0.24533
2025-02-06 13:29 | 0.44747 | 0.5081 | 26.4308 | 0.045208 | 0.97868 | 0.49161 | 0.0010641 | 43899.8819 | 0.023664 | 1.6966 | 32.1581 | 37.4565 | 2.7845 | 0.25113
2025-02-06 13:30 | 0.45249 | 0.5138 | 26.4301 | 0.045441 | 0.97868 | 0.49712 | 0.001076 | 44392.1337 | 0.023664 | 1.6966 | 32.4681 | 37.8169 | 2.8285 | 0.2551
2025-02-06 13:31 | 0.46716 | 0.53045 | 26.4295 | 0.045508 | 0.97868 | 0.51324 | 0.0011109 | 45831.3077 | 0.023665 | 1.6966 | 33.3714 | 38.8685 | 2.9197 | 0.26332
2025-02-06 13:32 | 0.47449 | 0.53878 | 26.4294 | 0.045446 | 0.97868 | 0.5213 | 0.0011283 | 46550.9598 | 0.023665 | 1.6966 | 33.8215 | 39.3927 | 2.9591 | 0.26687
2025-02-06 13:33 | 0.46947 | 0.53309 | 26.4298 | 0.045517 | 0.97868 | 0.51578 | 0.0011164 | 46058.6648 | 0.023665 | 1.6966 | 33.5136 | 39.0345 | 2.934 | 0.26461
2025-02-06 13:34 | 0.46059 | 0.523 | 26.4303 | 0.04559 | 0.97868 | 0.50603 | 0.0010953 | 45187.5941 | 0.023664 | 1.6966 | 32.9678 | 38.3991 | 2.8861 | 0.26029
2025-02-06 13:35 | 0.46909 | 0.53265 | 26.4307 | 0.045585 | 0.97868 | 0.51536 | 0.0011155 | 46021.003 | 0.023664 | 1.6966 | 33.4899 | 39.0077 | 2.9362 | 0.26481
2025-02-06 13:36 | 0.4714 | 0.53528 | 26.4311 | 0.045928 | 0.97868 | 0.5179 | 0.001121 | 46248.3753 | 0.023664 | 1.6967 | 33.6321 | 39.1737 | 2.9722 | 0.26805
2025-02-06 13:37 | 0.47874 | 0.54361 | 26.4306 | 0.046047 | 0.97868 | 0.52596 | 0.0011384 | 46967.9086 | 0.023664 | 1.6966 | 34.0817 | 39.6969 | 3.0238 | 0.27271
2025-02-06 13:38 | 0.48299 | 0.54843 | 26.4293 | 0.046002 | 0.97868 | 0.53063 | 0.0011485 | 47384.2282 | 0.023665 | 1.6966 | 34.3416 | 39.9983 | 3.0461 | 0.27472
2025-02-06 13:39 | 0.45673 | 0.51861 | 26.428 | 0.046019 | 0.97869 | 0.50179 | 0.0010861 | 44808.2736 | 0.023666 | 1.6965 | 32.73 | 38.1201 | 2.8899 | 0.26063
2025-02-06 13:40 | 0.45596 | 0.51773 | 26.4267 | 0.046014 | 0.97869 | 0.50094 | 0.0010843 | 44732.2084 | 0.023667 | 1.6965 | 32.6824 | 38.0635 | 2.8848 | 0.26017
2025-02-06 13:41 | 0.46639 | 0.52957 | 26.4254 | 0.046329 | 0.97869 | 0.51239 | 0.0011091 | 45754.5556 | 0.023668 | 1.6964 | 33.3239 | 38.8095 | 2.9673 | 0.26762
2025-02-06 13:42 | 0.4772 | 0.54184 | 26.4259 | 0.046388 | 0.97869 | 0.52427 | 0.0011348 | 46815.1985 | 0.023667 | 1.6964 | 33.9871 | 39.5823 | 3.0365 | 0.27385
2025-02-06 13:43 | 0.46947 | 0.53308 | 26.4276 | 0.0462 | 0.97869 | 0.51578 | 0.0011164 | 46058.0984 | 0.023666 | 1.6965 | 33.5136 | 39.0324 | 2.9779 | 0.26857
2025-02-06 13:44 | 0.47411 | 0.53835 | 26.4293 | 0.046239 | 0.97868 | 0.52087 | 0.0011274 | 46513.0506 | 0.023665 | 1.6966 | 33.7979 | 39.365 | 3.0084 | 0.27132
2025-02-06 13:45 | 0.48994 | 0.55632 | 26.431 | 0.046416 | 0.97868 | 0.53826 | 0.0011651 | 48066.4581 | 0.023664 | 1.6966 | 34.7661 | 40.4944 | 3.1156 | 0.28099
2025-02-06 13:46 | 0.4799 | 0.54493 | 26.4327 | 0.046598 | 0.97868 | 0.52724 | 0.0011412 | 47082.0835 | 0.023663 | 1.6967 | 34.1526 | 39.7815 | 3.0671 | 0.27662
2025-02-06 13:47 | 0.48492 | 0.55063 | 26.4331 | 0.046552 | 0.97868 | 0.53275 | 0.0011531 | 47574.5932 | 0.023662 | 1.6967 | 34.4596 | 40.1394 | 3.0946 | 0.27909
2025-02-06 13:48 | 0.48994 | 0.55633 | 26.4325 | 0.046549 | 0.97868 | 0.53826 | 0.0011651 | 48066.8364 | 0.023663 | 1.6967 | 34.7661 | 40.4958 | 3.1246 | 0.2818
2025-02-06 13:49 | 0.48762 | 0.5537 | 26.4318 | 0.046632 | 0.97868 | 0.53572 | 0.0011596 | 47839.403 | 0.023663 | 1.6967 | 34.6247 | 40.3304 | 3.1161 | 0.28103
2025-02-06 13:50 | 0.50345 | 0.57167 | 26.4312 | 0.046762 | 0.97868 | 0.55311 | 0.0011972 | 49392.2138 | 0.023664 | 1.6967 | 35.5891 | 41.4532 | 3.2208 | 0.29048
2025-02-06 13:51 | 0.50268 | 0.57079 | 26.4305 | 0.046907 | 0.97868 | 0.55226 | 0.0011954 | 49316.2877 | 0.023664 | 1.6966 | 35.5422 | 41.3979 | 3.2261 | 0.29095
2025-02-06 13:52 | 0.49032 | 0.55676 | 26.4309 | 0.047113 | 0.97868 | 0.53869 | 0.001166 | 48104.2975 | 0.023664 | 1.6966 | 34.7896 | 40.5217 | 3.1647 | 0.28542
2025-02-06 13:53 | 0.48801 | 0.55414 | 26.4319 | 0.047175 | 0.97868 | 0.53614 | 0.0011605 | 47877.3116 | 0.023663 | 1.6967 | 34.6482 | 40.358 | 3.1548 | 0.28452
2025-02-06 13:54 | 0.48492 | 0.55063 | 26.433 | 0.047097 | 0.97868 | 0.53275 | 0.0011531 | 47574.5675 | 0.023662 | 1.6967 | 34.4596 | 40.1393 | 3.1308 | 0.28236
2025-02-06 13:55 | 0.49573 | 0.56291 | 26.4341 | 0.047578 | 0.97868 | 0.54463 | 0.0011788 | 48635.4288 | 0.023662 | 1.6968 | 35.1192 | 40.9087 | 3.2296 | 0.29127
2025-02-06 13:56 | 0.50152 | 0.56949 | 26.4351 | 0.047562 | 0.97867 | 0.55099 | 0.0011926 | 49203.8861 | 0.023661 | 1.6968 | 35.4717 | 41.3204 | 3.2644 | 0.29441
2025-02-06 13:57 | 0.50384 | 0.57212 | 26.4362 | 0.047572 | 0.97867 | 0.55353 | 0.0011981 | 49431.4439 | 0.02366 | 1.6969 | 35.6126 | 41.4855 | 3.2795 | 0.29577
2025-02-06 13:58 | 0.49573 | 0.56292 | 26.4373 | 0.047708 | 0.97867 | 0.54463 | 0.0011788 | 48636.2787 | 0.023659 | 1.6969 | 35.1192 | 40.9118 | 3.2387 | 0.29209
2025-02-06 13:59 | 0.50345 | 0.57169 | 26.4384 | 0.047653 | 0.97867 | 0.55311 | 0.0011972 | 49394.1425 | 0.023659 | 1.697 | 35.5891 | 41.4603 | 3.2829 | 0.29607
2025-02-06 14:00 | 0.5104 | 0.57959 | 26.4394 | 0.047746 | 0.97866 | 0.56074 | 0.0012137 | 50076.2557 | 0.023658 | 1.697 | 36.0112 | 41.9531 | 3.3324 | 0.30054
2025-02-06 14:01 | 0.51079 | 0.58003 | 26.4405 | 0.047804 | 0.97866 | 0.56117 | 0.0012146 | 50114.4257 | 0.023657 | 1.6971 | 36.0346 | 41.9814 | 3.3389 | 0.30113
2025-02-06 14:02 | 0.52082 | 0.59143 | 26.4416 | 0.04792 | 0.97866 | 0.5722 | 0.0012385 | 51099.5885 | 0.023656 | 1.6971 | 36.6428 | 42.6911 | 3.4094 | 0.30749
2025-02-06 14:03 | 0.50808 | 0.57697 | 26.4427 | 0.048284 | 0.97866 | 0.5582 | 0.0012082 | 49849.852 | 0.023656 | 1.6972 | 35.8706 | 41.7925 | 3.3557 | 0.30264
2025-02-06 14:04 | 0.4826 | 0.54803 | 26.4437 | 0.048238 | 0.97866 | 0.5302 | 0.0011476 | 47350.0587 | 0.023655 | 1.6972 | 34.318 | 39.9845 | 3.193 | 0.28797
2025-02-06 14:05 | 0.48685 | 0.55286 | 26.4448 | 0.048039 | 0.97865 | 0.53487 | 0.0011577 | 47767.0174 | 0.023654 | 1.6973 | 34.5775 | 40.2879 | 3.2065 | 0.28919
2025-02-06 14:06 | 0.49457 | 0.56163 | 26.4459 | 0.047966 | 0.97865 | 0.54335 | 0.0011761 | 48524.9046 | 0.023653 | 1.6973 | 35.0486 | 40.8379 | 3.2498 | 0.2931
2025-02-06 14:07 | 0.49032 | 0.55681 | 26.4467 | 0.048187 | 0.97865 | 0.53869 | 0.001166 | 48108.4329 | 0.023653 | 1.6974 | 34.7896 | 40.5369 | 3.2383 | 0.29206
2025-02-06 14:08 | 0.49573 | 0.56295 | 26.4474 | 0.048281 | 0.97865 | 0.54463 | 0.0011788 | 48638.9313 | 0.023652 | 1.6974 | 35.1192 | 40.9216 | 3.2786 | 0.29569
2025-02-06 14:09 | 0.49766 | 0.56514 | 26.448 | 0.048384 | 0.97865 | 0.54675 | 0.0011834 | 48828.5064 | 0.023652 | 1.6974 | 35.2368 | 41.0592 | 3.2978 | 0.29742
2025-02-06 14:10 | 0.50615 | 0.57479 | 26.4486 | 0.048494 | 0.97865 | 0.55608 | 0.0012036 | 49662.0614 | 0.023651 | 1.6974 | 35.7534 | 41.6618 | 3.3587 | 0.30292
2025-02-06 14:11 | 0.51812 | 0.58839 | 26.4493 | 0.048624 | 0.97864 | 0.56923 | 0.0012321 | 50836.5517 | 0.023651 | 1.6975 | 36.4793 | 42.5083 | 3.4432 | 0.31054
2025-02-06 14:12 | 0.53318 | 0.60549 | 26.4494 | 0.048764 | 0.97864 | 0.58577 | 0.0012679 | 52313.9579 | 0.023651 | 1.6975 | 37.3891 | 43.5687 | 3.5482 | 0.32
2025-02-06 14:13 | 0.5409 | 0.61425 | 26.4492 | 0.04884 | 0.97864 | 0.59425 | 0.0012863 | 53071.5201 | 0.023651 | 1.6975 | 37.8543 | 44.1105 | 3.6024 | 0.32489
2025-02-06 14:14 | 0.53086 | 0.60285 | 26.449 | 0.048966 | 0.97864 | 0.58322 | 0.0012624 | 52086.5478 | 0.023651 | 1.6975 | 37.2494 | 43.4054 | 3.5481 | 0.32
2025-02-06 14:15 | 0.53781 | 0.61074 | 26.4488 | 0.049276 | 0.97865 | 0.59086 | 0.0012789 | 52768.3456 | 0.023651 | 1.6974 | 37.6684 | 43.8934 | 3.6148 | 0.32601
2025-02-06 14:16 | 0.54939 | 0.6239 | 26.4486 | 0.049474 | 0.97865 | 0.60358 | 0.0013065 | 53904.7164 | 0.023651 | 1.6974 | 38.365 | 44.7049 | 3.7034 | 0.334
2025-02-06 14:17 | 0.54476 | 0.61864 | 26.4487 | 0.049446 | 0.97865 | 0.59849 | 0.0012954 | 53450.1916 | 0.023651 | 1.6974 | 38.0866 | 44.3807 | 3.6717 | 0.33114
2025-02-06 14:18 | 0.54399 | 0.61776 | 26.4492 | 0.049436 | 0.97864 | 0.59765 | 0.0012936 | 53374.5537 | 0.023651 | 1.6975 | 38.0401 | 44.327 | 3.6661 | 0.33064
2025-02-06 14:19 | 0.54669 | 0.62083 | 26.4496 | 0.049771 | 0.97864 | 0.60062 | 0.0013 | 53639.8481 | 0.023651 | 1.6975 | 38.2026 | 44.5168 | 3.7084 | 0.33445
2025-02-06 14:20 | 0.54862 | 0.62303 | 26.45 | 0.049871 | 0.97864 | 0.60274 | 0.0013046 | 53829.3789 | 0.02365 | 1.6975 | 38.3186 | 44.6524 | 3.7282 | 0.33624
2025-02-06 14:21 | 0.54746 | 0.62171 | 26.4505 | 0.05004 | 0.97864 | 0.60146 | 0.0013019 | 53715.8596 | 0.02365 | 1.6975 | 38.249 | 44.5718 | 3.7334 | 0.33671
2025-02-06 14:22 | 0.54978 | 0.62434 | 26.4513 | 0.050338 | 0.97864 | 0.60401 | 0.0013074 | 53943.3879 | 0.02365 | 1.6976 | 38.3882 | 44.7348 | 3.7708 | 0.34008
2025-02-06 14:23 | 0.56638 | 0.6432 | 26.4523 | 0.050455 | 0.97864 | 0.62225 | 0.0013469 | 55572.6197 | 0.023649 | 1.6976 | 39.383 | 45.8952 | 3.8877 | 0.35062
2025-02-06 14:24 | 0.57835 | 0.6568 | 26.4534 | 0.050441 | 0.97864 | 0.6354 | 0.0013753 | 56747.2855 | 0.023648 | 1.6977 | 40.0976 | 46.7293 | 3.9644 | 0.35754
2025-02-06 14:25 | 0.58375 | 0.66294 | 26.4545 | 0.050565 | 0.97863 | 0.64134 | 0.0013882 | 57277.9692 | 0.023647 | 1.6977 | 40.4197 | 47.1058 | 4.0095 | 0.36161
2025-02-06 14:26 | 0.57989 | 0.65856 | 26.4556 | 0.050657 | 0.97863 | 0.63709 | 0.001379 | 56899.4757 | 0.023646 | 1.6977 | 40.1897 | 46.8389 | 3.9917 | 0.36
2025-02-06 14:27 | 0.5687 | 0.64585 | 26.4563 | 0.050847 | 0.97863 | 0.62479 | 0.0013524 | 55801.0917 | 0.023646 | 1.6978 | 39.5215 | 46.0609 | 3.9335 | 0.35475
2025-02-06 14:28 | 0.56831 | 0.64541 | 26.4567 | 0.051074 | 0.97863 | 0.62437 | 0.0013514 | 55763.3402 | 0.023646 | 1.6978 | 39.4984 | 46.0345 | 3.9486 | 0.35611
2025-02-06 14:29 | 0.57719 | 0.6555 | 26.4571 | 0.051107 | 0.97863 | 0.63412 | 0.0013726 | 56634.7724 | 0.023645 | 1.6978 | 40.0286 | 46.6528 | 4.0096 | 0.36161
2025-02-06 14:30 | 0.5687 | 0.64585 | 26.4575 | 0.051214 | 0.97863 | 0.62479 | 0.0013524 | 55801.4812 | 0.023645 | 1.6978 | 39.5215 | 46.0623 | 3.9621 | 0.35733
2025-02-06 14:31 | 0.56445 | 0.64103 | 26.458 | 0.051606 | 0.97863 | 0.62013 | 0.0013423 | 55384.9006 | 0.023645 | 1.6979 | 39.2675 | 45.7668 | 3.9642 | 0.35752
2025-02-06 14:32 | 0.55055 | 0.62525 | 26.4588 | 0.052062 | 0.97862 | 0.60486 | 0.0013092 | 54021.3522 | 0.023644 | 1.6979 | 38.4345 | 44.7968 | 3.906 | 0.35227
2025-02-06 14:33 | 0.53318 | 0.60552 | 26.4599 | 0.052167 | 0.97862 | 0.58577 | 0.0012679 | 52316.9164 | 0.023643 | 1.6979 | 37.3891 | 43.5794 | 3.7969 | 0.34244
2025-02-06 14:34 | 0.54283 | 0.61649 | 26.4609 | 0.052465 | 0.97862 | 0.59637 | 0.0012909 | 53264.3115 | 0.023643 | 1.698 | 37.9705 | 44.2582 | 3.8842 | 0.35031
2025-02-06 14:35 | 0.54322 | 0.61693 | 26.462 | 0.052702 | 0.97862 | 0.5968 | 0.0012918 | 53302.5052 | 0.023642 | 1.698 | 37.9937 | 44.2864 | 3.9045 | 0.35213
2025-02-06 14:36 | 0.5436 | 0.61737 | 26.4631 | 0.052623 | 0.97862 | 0.59722 | 0.0012927 | 53340.6971 | 0.023641 | 1.6981 | 38.0169 | 44.3146 | 3.9014 | 0.35186
2025-02-06 14:37 | 0.54824 | 0.62263 | 26.4634 | 0.052724 | 0.97862 | 0.60231 | 0.0013037 | 53795.4015 | 0.023641 | 1.6981 | 38.2954 | 44.6395 | 3.9404 | 0.35538
2025-02-06 14:38 | 0.55441 | 0.62965 | 26.4633 | 0.052985 | 0.97862 | 0.6091 | 0.0013184 | 54401.5018 | 0.023641 | 1.6981 | 38.6662 | 45.0716 | 4.0021 | 0.36094
2025-02-06 14:39 | 0.53665 | 0.60948 | 26.4631 | 0.053233 | 0.97862 | 0.58959 | 0.0012762 | 52658.7907 | 0.023641 | 1.6981 | 37.5986 | 43.8269 | 3.8988 | 0.35162
2025-02-06 14:40 | 0.53627 | 0.60904 | 26.463 | 0.053454 | 0.97862 | 0.58916 | 0.0012752 | 52620.8621 | 0.023641 | 1.6981 | 37.5753 | 43.7997 | 3.9123 | 0.35284
2025-02-06 14:41 | 0.52623 | 0.59764 | 26.4628 | 0.053959 | 0.97862 | 0.57813 | 0.0012514 | 51635.8361 | 0.023641 | 1.6981 | 36.9696 | 43.0935 | 3.8792 | 0.34985
2025-02-06 14:42 | 0.52739 | 0.59895 | 26.4626 | 0.054377 | 0.97862 | 0.57941 | 0.0012541 | 51749.4461 | 0.023642 | 1.6981 | 37.0396 | 43.1749 | 3.9174 | 0.3533
2025-02-06 14:43 | 0.52507 | 0.59632 | 26.4625 | 0.054422 | 0.97862 | 0.57686 | 0.0012486 | 51522.1016 | 0.023642 | 1.6981 | 36.8996 | 43.0116 | 3.9043 | 0.35212
2025-02-06 14:44 | 0.51426 | 0.58404 | 26.463 | 0.054731 | 0.97862 | 0.56499 | 0.0012229 | 50461.4807 | 0.023641 | 1.6981 | 36.2454 | 42.2494 | 3.8499 | 0.34721
2025-02-06 14:45 | 0.50847 | 0.57747 | 26.4638 | 0.055271 | 0.97861 | 0.55862 | 0.0012091 | 49893.4526 | 0.023641 | 1.6981 | 35.8941 | 41.8408 | 3.8464 | 0.3469
2025-02-06 14:46 | 0.50036 | 0.56827 | 26.4647 | 0.055327 | 0.97861 | 0.54972 | 0.0011899 | 49098.1131 | 0.02364 | 1.6982 | 35.4013 | 41.2672 | 3.7922 | 0.34201
2025-02-06 14:47 | 0.49843 | 0.56608 | 26.4655 | 0.055417 | 0.97861 | 0.54759 | 0.0011853 | 48908.9183 | 0.023639 | 1.6982 | 35.2838 | 41.1311 | 3.7846 | 0.34132
2025-02-06 14:48 | 0.50924 | 0.57836 | 26.4664 | 0.055825 | 0.97861 | 0.55947 | 0.001211 | 49969.9151 | 0.023639 | 1.6982 | 35.9409 | 41.898 | 3.8909 | 0.35091
2025-02-06 14:49 | 0.52237 | 0.59327 | 26.4669 | 0.055959 | 0.97861 | 0.57389 | 0.0012422 | 51258.125 | 0.023639 | 1.6983 | 36.7363 | 42.8256 | 3.9955 | 0.36034
2025-02-06 14:50 | 0.52005 | 0.59064 | 26.4671 | 0.056076 | 0.97861 | 0.57135 | 0.0012367 | 51030.8762 | 0.023638 | 1.6983 | 36.5961 | 42.6624 | 3.987 | 0.35958
2025-02-06 14:51 | 0.5243 | 0.59546 | 26.4673 | 0.056369 | 0.97861 | 0.57601 | 0.0012468 | 51447.6675 | 0.023638 | 1.6983 | 36.853 | 42.9621 | 4.0389 | 0.36426
2025-02-06 14:52 | 0.51696 | 0.58713 | 26.4675 | 0.056792 | 0.97861 | 0.56795 | 0.0012293 | 50727.9153 | 0.023638 | 1.6983 | 36.4091 | 42.4449 | 4.0153 | 0.36213
2025-02-06 14:53 | 0.51426 | 0.58406 | 26.4677 | 0.056953 | 0.97861 | 0.56499 | 0.0012229 | 50462.7824 | 0.023638 | 1.6983 | 36.2454 | 42.2542 | 4.0067 | 0.36136
2025-02-06 14:54 | 0.51426 | 0.58406 | 26.4685 | 0.057143 | 0.97861 | 0.56499 | 0.0012229 | 50462.9852 | 0.023637 | 1.6983 | 36.2454 | 42.2549 | 4.0202 | 0.36257
2025-02-06 14:55 | 0.51426 | 0.58407 | 26.4695 | 0.057356 | 0.9786 | 0.56499 | 0.0012229 | 50463.2799 | 0.023637 | 1.6984 | 36.2454 | 42.256 | 4.0353 | 0.36393
2025-02-06 14:56 | 0.51426 | 0.58407 | 26.4706 | 0.057716 | 0.9786 | 0.56499 | 0.0012229 | 50463.5745 | 0.023636 | 1.6984 | 36.2454 | 42.2571 | 4.0607 | 0.36623
2025-02-06 14:57 | 0.51426 | 0.58407 | 26.4717 | 0.057957 | 0.9786 | 0.56499 | 0.0012229 | 50463.8692 | 0.023635 | 1.6985 | 36.2454 | 42.2582 | 4.0778 | 0.36777
2025-02-06 14:58 | 0.5104 | 0.57969 | 26.4728 | 0.057996 | 0.9786 | 0.56074 | 0.0012137 | 50085.2999 | 0.023634 | 1.6985 | 36.0112 | 41.9862 | 4.0517 | 0.36541
2025-02-06 14:59 | 0.50885 | 0.57794 | 26.4732 | 0.057903 | 0.9786 | 0.55905 | 0.0012101 | 49933.8647 | 0.023634 | 1.6985 | 35.9175 | 41.8774 | 4.0336 | 0.36378
2025-02-06 15:00 | 0.51426 | 0.58408 | 26.4732 | 0.058016 | 0.9786 | 0.56499 | 0.0012229 | 50464.2719 | 0.023634 | 1.6985 | 36.2454 | 42.2596 | 4.0821 | 0.36816
2025-02-06 15:01 | 0.51233 | 0.58188 | 26.4732 | 0.058204 | 0.9786 | 0.56286 | 0.0012183 | 50274.8408 | 0.023634 | 1.6985 | 36.1283 | 42.1232 | 4.0808 | 0.36804
2025-02-06 15:02 | 0.51542 | 0.58539 | 26.4732 | 0.058363 | 0.9786 | 0.56626 | 0.0012257 | 50577.9288 | 0.023634 | 1.6985 | 36.3156 | 42.3415 | 4.1153 | 0.37115
2025-02-06 15:03 | 0.51967 | 0.59022 | 26.4732 | 0.058603 | 0.9786 | 0.57092 | 0.0012358 | 50994.6767 | 0.023634 | 1.6985 | 36.5727 | 42.6413 | 4.1645 | 0.37559
2025-02-06 15:04 | 0.51619 | 0.58627 | 26.4732 | 0.059155 | 0.9786 | 0.56711 | 0.0012275 | 50653.7013 | 0.023634 | 1.6985 | 36.3623 | 42.396 | 4.1771 | 0.37672
2025-02-06 15:05 | 0.52082 | 0.59153 | 26.4732 | 0.059075 | 0.9786 | 0.5722 | 0.0012385 | 51108.3346 | 0.023634 | 1.6985 | 36.6428 | 42.7231 | 4.2069 | 0.37941
2025-02-06 15:06 | 0.52739 | 0.59899 | 26.4734 | 0.058902 | 0.97859 | 0.57941 | 0.0012541 | 51752.474 | 0.023634 | 1.6986 | 37.0396 | 43.1859 | 4.2447 | 0.38282
2025-02-06 15:07 | 3.6118 | 4.1021 | 26.4739 | 0.058976 | 0.97859 | 3.968 | 0.0085888 | 354425.7075 | 0.023634 | 1.6986 | 193.7655 | 225.9212 | 25.9151 | 2.3372
2025-02-06 15:08 | 5.2912 | 6.0096 | 26.4743 | 0.059071 | 0.97859 | 5.8132 | 0.012583 | 519232.0301 | 0.023633 | 1.6986 | 269.0882 | 313.747 | 37.0345 | 3.3401
2025-02-06 15:09 | 1.3934 | 1.5825 | 26.4747 | 0.05901 | 0.97859 | 1.5308 | 0.0033134 | 136732.0533 | 0.023633 | 1.6986 | 85.4145 | 99.5912 | 10.634 | 0.95906
2025-02-06 15:10 | 0.84243 | 0.95681 | 26.4752 | 0.059261 | 0.97859 | 0.92552 | 0.0020033 | 82668.3389 | 0.023633 | 1.6986 | 55.4107 | 64.6082 | 6.6497 | 0.59972
2025-02-06 15:11 | 0.48723 | 0.55339 | 26.4756 | 0.059521 | 0.97859 | 0.53529 | 0.0011586 | 47812.8714 | 0.023632 | 1.6986 | 34.6011 | 40.3448 | 3.9795 | 0.3589
2025-02-06 15:12 | 0.48762 | 0.55383 | 26.476 | 0.059582 | 0.97859 | 0.53572 | 0.0011596 | 47850.8681 | 0.023632 | 1.6987 | 34.6247 | 40.3727 | 3.9865 | 0.35954
2025-02-06 15:13 | 0.48608 | 0.55208 | 26.4764 | 0.059662 | 0.97859 | 0.53402 | 0.0011559 | 47699.4333 | 0.023632 | 1.6987 | 34.5303 | 40.2632 | 3.98 | 0.35894
2025-02-06 15:14 | 0.47449 | 0.53892 | 26.4769 | 0.059872 | 0.97859 | 0.5213 | 0.0011283 | 46562.9399 | 0.023631 | 1.6987 | 33.8215 | 39.4371 | 3.9038 | 0.35207
2025-02-06 15:15 | 0.48492 | 0.55076 | 26.4773 | 0.060161 | 0.97859 | 0.53275 | 0.0011531 | 47585.9964 | 0.023631 | 1.6987 | 34.4596 | 40.1815 | 4.0043 | 0.36114
2025-02-06 15:16 | 0.49766 | 0.56524 | 26.4778 | 0.060154 | 0.97859 | 0.54675 | 0.0011834 | 48836.3841 | 0.023631 | 1.6987 | 35.2368 | 41.0882 | 4.1036 | 0.37009
2025-02-06 15:17 | 0.49264 | 0.55954 | 26.4782 | 0.060422 | 0.97859 | 0.54123 | 0.0011715 | 48343.9731 | 0.023631 | 1.6988 | 34.9309 | 40.732 | 4.0825 | 0.36819
2025-02-06 15:18 | 0.49148 | 0.55822 | 26.4787 | 0.060846 | 0.97858 | 0.53996 | 0.0011687 | 48230.4305 | 0.02363 | 1.6988 | 34.8603 | 40.6501 | 4.102 | 0.36995
2025-02-06 15:19 | 0.50113 | 0.56919 | 26.4791 | 0.061299 | 0.97858 | 0.55056 | 0.0011917 | 49177.734 | 0.02363 | 1.6988 | 35.4483 | 41.3361 | 4.2095 | 0.37964
2025-02-06 15:20 | 0.49573 | 0.56305 | 26.4796 | 0.061164 | 0.97858 | 0.54463 | 0.0011788 | 48647.4334 | 0.02363 | 1.6988 | 35.1192 | 40.9529 | 4.1573 | 0.37494
2025-02-06 15:21 | 0.48801 | 0.55428 | 26.4801 | 0.06141 | 0.97858 | 0.53614 | 0.0011605 | 47889.8053 | 0.023629 | 1.6988 | 34.6482 | 40.4041 | 4.1124 | 0.37089
2025-02-06 15:22 | 0.48492 | 0.55077 | 26.4805 | 0.061765 | 0.97858 | 0.53275 | 0.0011531 | 47586.8223 | 0.023629 | 1.6989 | 34.4596 | 40.1845 | 4.1115 | 0.3708
2025-02-06 15:23 | 0.50345 | 0.57182 | 26.4805 | 0.061659 | 0.97858 | 0.55311 | 0.0011972 | 49405.4348 | 0.023629 | 1.6989 | 35.5891 | 41.5018 | 4.2529 | 0.38356
2025-02-06 15:24 | 0.50847 | 0.57752 | 26.4803 | 0.061815 | 0.97858 | 0.55862 | 0.0012091 | 49897.9168 | 0.023629 | 1.6989 | 35.8941 | 41.8571 | 4.3039 | 0.38816
2025-02-06 15:25 | 0.50615 | 0.57489 | 26.4801 | 0.062072 | 0.97858 | 0.55608 | 0.0012036 | 49670.5335 | 0.023629 | 1.6989 | 35.7534 | 41.6929 | 4.3032 | 0.38809
2025-02-06 15:26 | 0.50654 | 0.57533 | 26.4799 | 0.062396 | 0.97858 | 0.5565 | 0.0012046 | 49708.3627 | 0.023629 | 1.6988 | 35.7768 | 41.72 | 4.3287 | 0.39039
2025-02-06 15:27 | 0.49959 | 0.56743 | 26.4797 | 0.062438 | 0.97858 | 0.54887 | 0.001188 | 49026.3318 | 0.02363 | 1.6988 | 35.3543 | 41.2271 | 4.2752 | 0.38557
2025-02-06 15:28 | 0.50885 | 0.57796 | 26.48 | 0.062769 | 0.97858 | 0.55905 | 0.0012101 | 49935.7218 | 0.023629 | 1.6988 | 35.9175 | 41.8842 | 4.3735 | 0.39443
2025-02-06 15:29 | 0.51426 | 0.5841 | 26.4807 | 0.062978 | 0.97858 | 0.56499 | 0.0012229 | 50466.3256 | 0.023629 | 1.6989 | 36.2454 | 42.2671 | 4.4323 | 0.39974
2025-02-06 15:30 | 0.51426 | 0.5841 | 26.4813 | 0.063005 | 0.97858 | 0.56499 | 0.0012229 | 50466.5023 | 0.023628 | 1.6989 | 36.2454 | 42.2678 | 4.4342 | 0.39991
2025-02-06 15:31 | 0.50847 | 0.57753 | 26.482 | 0.062944 | 0.97858 | 0.55862 | 0.0012091 | 49898.3603 | 0.023628 | 1.6989 | 35.8941 | 41.8588 | 4.3827 | 0.39527
2025-02-06 15:32 | 0.51194 | 0.58148 | 26.4826 | 0.063061 | 0.97858 | 0.56244 | 0.0012174 | 50239.5249 | 0.023627 | 1.699 | 36.1049 | 42.1053 | 4.4194 | 0.39857
2025-02-06 15:33 | 0.52816 | 0.5999 | 26.4831 | 0.063586 | 0.97858 | 0.58026 | 0.001256 | 51830.9624 | 0.023627 | 1.699 | 37.0862 | 43.2502 | 4.5898 | 0.41394
2025-02-06 15:34 | 0.52237 | 0.59332 | 26.4835 | 0.064251 | 0.97857 | 0.57389 | 0.0012422 | 51262.7612 | 0.023627 | 1.699 | 36.7363 | 42.8425 | 4.5897 | 0.41394
2025-02-06 15:35 | 0.51426 | 0.58411 | 26.484 | 0.065 | 0.97857 | 0.56499 | 0.0012229 | 50467.2281 | 0.023626 | 1.699 | 36.2454 | 42.2705 | 4.575 | 0.4126
2025-02-06 15:36 | 0.50847 | 0.57753 | 26.4844 | 0.065823 | 0.97857 | 0.55862 | 0.0012091 | 49899.0193 | 0.023626 | 1.699 | 35.8941 | 41.8612 | 4.5835 | 0.41338
2025-02-06 15:37 | 0.49843 | 0.56613 | 26.4848 | 0.066517 | 0.97857 | 0.54759 | 0.0011853 | 48914.0336 | 0.023626 | 1.6991 | 35.2838 | 41.1499 | 4.5452 | 0.40992
2025-02-06 15:38 | 0.49766 | 0.56526 | 26.4852 | 0.067417 | 0.97857 | 0.54675 | 0.0011834 | 48838.37 | 0.023626 | 1.6991 | 35.2368 | 41.0955 | 4.6 | 0.41486
2025-02-06 15:39 | 0.50422 | 0.57272 | 26.4857 | 0.068155 | 0.97857 | 0.55396 | 0.001199 | 49482.5916 | 0.023625 | 1.6991 | 35.6361 | 41.5616 | 4.7085 | 0.42465
2025-02-06 15:40 | 0.51542 | 0.58543 | 26.4861 | 0.068811 | 0.97857 | 0.56626 | 0.0012257 | 50581.4804 | 0.023625 | 1.6991 | 36.3156 | 42.3545 | 4.8539 | 0.43776
2025-02-06 15:41 | 0.51967 | 0.59026 | 26.4865 | 0.069334 | 0.97857 | 0.57092 | 0.0012358 | 50998.3762 | 0.023625 | 1.6991 | 36.5727 | 42.6549 | 4.929 | 0.44453
2025-02-06 15:42 | 0.53163 | 0.60385 | 26.487 | 0.069886 | 0.97857 | 0.58407 | 0.0012642 | 52173.0557 | 0.023624 | 1.6992 | 37.296 | 43.4988 | 5.0766 | 0.45785
2025-02-06 15:43 | 0.54051 | 0.61394 | 26.4881 | 0.070426 | 0.97856 | 0.59383 | 0.0012853 | 53044.8247 | 0.023624 | 1.6992 | 37.8311 | 44.1241 | 5.1969 | 0.4687
2025-02-06 15:44 | 0.50924 | 0.57843 | 26.4896 | 0.070611 | 0.97856 | 0.55947 | 0.001211 | 49976.2095 | 0.023623 | 1.6993 | 35.9409 | 41.921 | 4.9247 | 0.44415
2025-02-06 15:45 | 0.50345 | 0.57185 | 26.4911 | 0.07098 | 0.97856 | 0.55311 | 0.0011972 | 49408.2712 | 0.023621 | 1.6993 | 35.5891 | 41.5122 | 4.8973 | 0.44168
2025-02-06 15:46 | 0.50268 | 0.57098 | 26.4926 | 0.071228 | 0.97856 | 0.55226 | 0.0011954 | 49332.8945 | 0.02362 | 1.6994 | 35.5422 | 41.4589 | 4.9075 | 0.4426
2025-02-06 15:47 | 0.49225 | 0.55915 | 26.4941 | 0.071375 | 0.97855 | 0.54081 | 0.0011706 | 48310.2514 | 0.023619 | 1.6995 | 34.9074 | 40.7199 | 4.8212 | 0.43481
2025-02-06 15:48 | 0.50036 | 0.56836 | 26.4949 | 0.071452 | 0.97855 | 0.54972 | 0.0011899 | 49106.164 | 0.023619 | 1.6995 | 35.4013 | 41.2968 | 4.9018 | 0.44208
2025-02-06 15:49 | 0.49843 | 0.56617 | 26.4953 | 0.071604 | 0.97855 | 0.54759 | 0.0011853 | 48916.8248 | 0.023618 | 1.6995 | 35.2838 | 41.1602 | 4.8943 | 0.4414
2025-02-06 15:50 | 0.50345 | 0.57187 | 26.4958 | 0.071673 | 0.97855 | 0.55311 | 0.0011972 | 49409.5187 | 0.023618 | 1.6996 | 35.5891 | 41.5168 | 4.9458 | 0.44605
2025-02-06 15:51 | 0.50654 | 0.57538 | 26.4962 | 0.071608 | 0.97855 | 0.5565 | 0.0012046 | 49712.7611 | 0.023618 | 1.6996 | 35.7768 | 41.7362 | 4.9701 | 0.44824
2025-02-06 15:52 | 0.51117 | 0.58064 | 26.4966 | 0.071511 | 0.97855 | 0.56159 | 0.0012156 | 50167.568 | 0.023618 | 1.6996 | 36.0581 | 42.0647 | 5.0064 | 0.45152
2025-02-06 15:53 | 0.52314 | 0.59424 | 26.4972 | 0.071422 | 0.97855 | 0.57474 | 0.001244 | 51342.3463 | 0.023617 | 1.6996 | 36.7829 | 42.9109 | 5.1111 | 0.46096
2025-02-06 15:54 | 0.51156 | 0.58109 | 26.4978 | 0.071387 | 0.97855 | 0.56202 | 0.0012165 | 50205.7915 | 0.023617 | 1.6996 | 36.0815 | 42.0932 | 5.0015 | 0.45107
2025-02-06 15:55 | 0.5104 | 0.57977 | 26.4985 | 0.071228 | 0.97854 | 0.56074 | 0.0012137 | 50092.2925 | 0.023616 | 1.6997 | 36.0112 | 42.0119 | 4.9797 | 0.44911
2025-02-06 15:56 | 0.51079 | 0.58021 | 26.4991 | 0.071336 | 0.97854 | 0.56117 | 0.0012146 | 50130.3571 | 0.023616 | 1.6997 | 36.0346 | 42.0398 | 4.991 | 0.45012
2025-02-06 15:57 | 0.5131 | 0.58285 | 26.4998 | 0.071164 | 0.97854 | 0.56371 | 0.0012202 | 50357.8768 | 0.023615 | 1.6997 | 36.1751 | 42.2044 | 5.0004 | 0.45098
2025-02-06 15:58 | 0.50113 | 0.56925 | 26.4997 | 0.070999 | 0.97854 | 0.55056 | 0.0011917 | 49183.2193 | 0.023615 | 1.6997 | 35.4483 | 41.3563 | 4.8785 | 0.43998
2025-02-06 15:59 | 0.50731 | 0.57627 | 26.4993 | 0.070919 | 0.97854 | 0.55735 | 0.0012064 | 49789.3693 | 0.023616 | 1.6997 | 35.8237 | 41.7939 | 4.9299 | 0.44461
2025-02-06 16:00 | 0.51194 | 0.58153 | 26.4988 | 0.070707 | 0.97854 | 0.56244 | 0.0012174 | 50243.95 | 0.023616 | 1.6997 | 36.1049 | 42.1215 | 4.9575 | 0.44711
2025-02-06 16:01 | 0.49959 | 0.56749 | 26.4984 | 0.070338 | 0.97854 | 0.54887 | 0.001188 | 49031.3108 | 0.023616 | 1.6997 | 35.3543 | 41.2454 | 4.8187 | 0.43459
2025-02-06 16:02 | 0.51465 | 0.58459 | 26.498 | 0.070192 | 0.97854 | 0.56541 | 0.0012238 | 50508.9583 | 0.023617 | 1.6997 | 36.2688 | 42.3118 | 4.9459 | 0.44606
2025-02-06 16:03 | 0.52044 | 0.59117 | 26.4984 | 0.070236 | 0.97854 | 0.57177 | 0.0012376 | 51077.4459 | 0.023616 | 1.6997 | 36.6195 | 42.7214 | 5.0018 | 0.4511
2025-02-06 16:04 | 0.51156 | 0.58109 | 26.4993 | 0.069797 | 0.97854 | 0.56202 | 0.0012165 | 50206.182 | 0.023616 | 1.6997 | 36.0815 | 42.0946 | 4.8903 | 0.44105
2025-02-06 16:05 | 0.52391 | 0.59513 | 26.5001 | 0.069514 | 0.97854 | 0.57559 | 0.0012459 | 51418.9491 | 0.023615 | 1.6998 | 36.8296 | 42.9683 | 4.982 | 0.44931
2025-02-06 16:06 | 0.54129 | 0.61486 | 26.501 | 0.069241 | 0.97854 | 0.59468 | 0.0012872 | 53124.3197 | 0.023615 | 1.6998 | 37.8776 | 44.1918 | 5.1183 | 0.4616
2025-02-06 16:07 | 0.53704 | 0.61004 | 26.5018 | 0.068885 | 0.97854 | 0.59001 | 0.0012771 | 52707.7521 | 0.023614 | 1.6998 | 37.6218 | 43.8944 | 5.0542 | 0.45583
2025-02-06 16:08 | 0.51967 | 0.59031 | 26.5023 | 0.068577 | 0.97854 | 0.57092 | 0.0012358 | 51002.749 | 0.023614 | 1.6999 | 36.5727 | 42.6709 | 4.8773 | 0.43988
2025-02-06 16:09 | 0.51426 | 0.58417 | 26.5026 | 0.068262 | 0.97854 | 0.56499 | 0.0012229 | 50472.3445 | 0.023613 | 1.6999 | 36.2454 | 42.2892 | 4.8071 | 0.43355
2025-02-06 16:10 | 0.52005 | 0.59075 | 26.503 | 0.068046 | 0.97853 | 0.57135 | 0.0012367 | 51040.8104 | 0.023613 | 1.6999 | 36.5961 | 42.6987 | 4.8431 | 0.43679
2025-02-06 16:11 | 0.53009 | 0.60215 | 26.5033 | 0.06789 | 0.97853 | 0.58238 | 0.0012606 | 52026.0934 | 0.023613 | 1.6999 | 37.2028 | 43.4069 | 4.9203 | 0.44375
2025-02-06 16:12 | 0.53279 | 0.60522 | 26.5036 | 0.067689 | 0.97853 | 0.58535 | 0.001267 | 52291.4275 | 0.023613 | 1.6999 | 37.3658 | 43.5975 | 4.9295 | 0.44458
2025-02-06 16:13 | 0.53279 | 0.60523 | 26.5039 | 0.067328 | 0.97853 | 0.58535 | 0.001267 | 52291.5147 | 0.023612 | 1.6999 | 37.3658 | 43.5978 | 4.9033 | 0.44222
2025-02-06 16:14 | 0.53279 | 0.60523 | 26.5042 | 0.067149 | 0.97853 | 0.58535 | 0.001267 | 52291.599 | 0.023612 | 1.6999 | 37.3658 | 43.5981 | 4.8903 | 0.44104
2025-02-06 16:15 | 0.53086 | 0.60303 | 26.5041 | 0.066825 | 0.97853 | 0.58322 | 0.0012624 | 52102.1225 | 0.023612 | 1.6999 | 37.2494 | 43.4622 | 4.85 | 0.43741
2025-02-06 16:16 | 0.54553 | 0.6197 | 26.5039 | 0.066493 | 0.97853 | 0.59934 | 0.0012973 | 53541.9735 | 0.023612 | 1.6999 | 38.133 | 44.4929 | 4.952 | 0.44661
2025-02-06 16:17 | 0.57565 | 0.65391 | 26.5037 | 0.066275 | 0.97853 | 0.63243 | 0.0013689 | 56497.5176 | 0.023613 | 1.6999 | 39.9365 | 46.5969 | 5.1934 | 0.46838
2025-02-06 16:18 | 0.57217 | 0.64996 | 26.5035 | 0.066071 | 0.97853 | 0.62861 | 0.0013606 | 56156.4207 | 0.023613 | 1.6999 | 39.7291 | 46.3547 | 5.1477 | 0.46426
2025-02-06 16:19 | 0.56947 | 0.64689 | 26.5033 | 0.065718 | 0.97853 | 0.62564 | 0.0013542 | 55891.1119 | 0.023613 | 1.6999 | 39.5676 | 46.1661 | 5.0974 | 0.45972
2025-02-06 16:20 | 0.56522 | 0.64206 | 26.5035 | 0.06527 | 0.97853 | 0.62098 | 0.0013441 | 55474.364 | 0.023613 | 1.6999 | 39.3137 | 45.8701 | 5.0269 | 0.45336
2025-02-06 16:21 | 0.53279 | 0.60523 | 26.5039 | 0.064895 | 0.97853 | 0.58535 | 0.001267 | 52291.5309 | 0.023612 | 1.6999 | 37.3658 | 43.5978 | 4.7261 | 0.42623
2025-02-06 16:22 | 0.53279 | 0.60523 | 26.5044 | 0.064438 | 0.97853 | 0.58535 | 0.001267 | 52291.6527 | 0.023612 | 1.6999 | 37.3658 | 43.5983 | 4.6928 | 0.42323
2025-02-06 16:23 | 0.5463 | 0.62058 | 26.5048 | 0.064234 | 0.97853 | 0.60019 | 0.0012991 | 53618.0148 | 0.023612 | 1.7 | 38.1794 | 44.548 | 4.7903 | 0.43203
2025-02-06 16:24 | 0.5575 | 0.6333 | 26.5052 | 0.063836 | 0.97853 | 0.61249 | 0.0013257 | 54717.025 | 0.023612 | 1.7 | 38.8514 | 45.3325 | 4.853 | 0.43768
2025-02-06 16:25 | 0.55441 | 0.62979 | 26.5053 | 0.063429 | 0.97853 | 0.6091 | 0.0013184 | 54413.9244 | 0.023611 | 1.7 | 38.6662 | 45.1166 | 4.7969 | 0.43262
2025-02-06 16:26 | 0.57294 | 0.65084 | 26.5053 | 0.062967 | 0.97853 | 0.62946 | 0.0013625 | 56232.7743 | 0.023611 | 1.7 | 39.7752 | 46.4105 | 4.9125 | 0.44304
2025-02-06 16:27 | 0.58375 | 0.66312 | 26.5053 | 0.062462 | 0.97853 | 0.64134 | 0.0013882 | 57293.7716 | 0.023611 | 1.7 | 40.4197 | 47.1626 | 4.96 | 0.44733
2025-02-06 16:28 | 0.58375 | 0.66312 | 26.5053 | 0.06204 | 0.97853 | 0.64134 | 0.0013882 | 57293.7716 | 0.023611 | 1.7 | 40.4197 | 47.1626 | 4.9265 | 0.44431
2025-02-06 16:29 | 0.56638 | 0.64339 | 26.5053 | 0.061517 | 0.97853 | 0.62225 | 0.0013469 | 55588.5988 | 0.023611 | 1.7 | 39.383 | 45.953 | 4.7473 | 0.42815
2025-02-06 16:30 | 0.55364 | 0.62891 | 26.5053 | 0.061093 | 0.97853 | 0.60825 | 0.0013166 | 54338.1387 | 0.023611 | 1.7 | 38.6199 | 45.0626 | 4.6141 | 0.41613
2025-02-06 16:31 | 0.57372 | 0.65172 | 26.5053 | 0.060644 | 0.97853 | 0.63031 | 0.0013643 | 56308.56 | 0.023611 | 1.7 | 39.8213 | 46.4643 | 4.7373 | 0.42724
2025-02-06 16:32 | 0.5907 | 0.67102 | 26.5053 | 0.060286 | 0.97853 | 0.64897 | 0.0014047 | 57975.8392 | 0.023611 | 1.7 | 40.8332 | 47.6451 | 4.8412 | 0.43662
2025-02-06 16:33 | 0.61271 | 0.69602 | 26.5053 | 0.060019 | 0.97853 | 0.67315 | 0.001457 | 60135.723 | 0.023611 | 1.7 | 42.1381 | 49.1677 | 4.9894 | 0.44999
2025-02-06 16:34 | 0.58993 | 0.67014 | 26.5053 | 0.059663 | 0.97853 | 0.64812 | 0.0014029 | 57900.0525 | 0.023611 | 1.7 | 40.7873 | 47.5915 | 4.7852 | 0.43157
2025-02-06 16:35 | 0.55441 | 0.62979 | 26.5053 | 0.059285 | 0.97853 | 0.6091 | 0.0013184 | 54413.9244 | 0.023611 | 1.7 | 38.6662 | 45.1166 | 4.4835 | 0.40435
2025-02-06 16:36 | 0.56715 | 0.64426 | 26.5053 | 0.058958 | 0.97853 | 0.6231 | 0.0013487 | 55664.3834 | 0.023611 | 1.7 | 39.4292 | 46.0068 | 4.5556 | 0.41086
2025-02-06 16:37 | 0.57565 | 0.65391 | 26.5053 | 0.05877 | 0.97853 | 0.63243 | 0.0013689 | 56498.0243 | 0.023611 | 1.7 | 39.9365 | 46.5988 | 4.6055 | 0.41536
2025-02-06 16:38 | 0.58955 | 0.6697 | 26.5054 | 0.058498 | 0.97853 | 0.6477 | 0.0014019 | 57862.1622 | 0.023611 | 1.7 | 40.7643 | 47.5647 | 4.6888 | 0.42288
2025-02-06 16:39 | 0.588 | 0.66795 | 26.5055 | 0.058105 | 0.97853 | 0.646 | 0.0013983 | 57710.636 | 0.023611 | 1.7 | 40.6725 | 47.4577 | 4.6459 | 0.419
2025-02-06 16:40 | 0.56098 | 0.63725 | 26.5057 | 0.057801 | 0.97853 | 0.61631 | 0.001334 | 55058.2088 | 0.023611 | 1.7 | 39.0595 | 45.576 | 4.4202 | 0.39865
2025-02-06 16:41 | 0.55943 | 0.63549 | 26.5059 | 0.057571 | 0.97853 | 0.61461 | 0.0013303 | 54906.7032 | 0.023611 | 1.7 | 38.9671 | 45.4683 | 4.3912 | 0.39603
2025-02-06 16:42 | 0.58568 | 0.66532 | 26.5061 | 0.057171 | 0.97853 | 0.64346 | 0.0013928 | 57483.4826 | 0.023611 | 1.7 | 40.5346 | 47.2976 | 4.5542 | 0.41073
2025-02-06 16:43 | 0.5575 | 0.6333 | 26.5063 | 0.056965 | 0.97853 | 0.61249 | 0.0013257 | 54717.3636 | 0.023611 | 1.7 | 38.8514 | 45.3338 | 4.3308 | 0.39059
2025-02-06 16:44 | 0.51619 | 0.58637 | 26.5063 | 0.056764 | 0.97853 | 0.56711 | 0.0012275 | 50662.7995 | 0.023611 | 1.7 | 36.3623 | 42.4293 | 4.0121 | 0.36184
2025-02-06 16:45 | 0.51889 | 0.58944 | 26.5061 | 0.056392 | 0.97853 | 0.57008 | 0.0012339 | 50927.9887 | 0.023611 | 1.7 | 36.526 | 42.6201 | 4.0055 | 0.36125
2025-02-06 16:46 | 0.51889 | 0.58944 | 26.5058 | 0.056116 | 0.97853 | 0.57008 | 0.0012339 | 50927.9293 | 0.023611 | 1.7 | 36.526 | 42.6199 | 3.9859 | 0.35948
2025-02-06 16:47 | 0.52468 | 0.59602 | 26.5056 | 0.055857 | 0.97853 | 0.57644 | 0.0012477 | 51496.2616 | 0.023611 | 1.7 | 36.8763 | 43.0284 | 4.0094 | 0.3616
2025-02-06 16:48 | 0.53086 | 0.60304 | 26.5054 | 0.055762 | 0.97853 | 0.58322 | 0.0012624 | 52102.4863 | 0.023611 | 1.7 | 37.2494 | 43.4635 | 4.0472 | 0.36501
2025-02-06 16:49 | 0.53009 | 0.60216 | 26.5053 | 0.055691 | 0.97853 | 0.58238 | 0.0012606 | 52026.6828 | 0.023611 | 1.7 | 37.2028 | 43.409 | 4.0364 | 0.36404
2025-02-06 16:50 | 0.53858 | 0.61181 | 26.5053 | 0.055742 | 0.97853 | 0.59171 | 0.0012808 | 52860.3237 | 0.023611 | 1.7 | 37.7149 | 44.0066 | 4.1015 | 0.3699
2025-02-06 16:51 | 0.5409 | 0.61444 | 26.5053 | 0.055718 | 0.97853 | 0.59425 | 0.0012863 | 53087.6801 | 0.023611 | 1.7 | 37.8543 | 44.1693 | 4.1164 | 0.37125
2025-02-06 16:52 | 0.53858 | 0.61181 | 26.5053 | 0.055643 | 0.97853 | 0.59171 | 0.0012808 | 52860.3237 | 0.023611 | 1.7 | 37.7149 | 44.0066 | 4.0942 | 0.36924
2025-02-06 16:53 | 0.53897 | 0.61225 | 26.5053 | 0.055345 | 0.97853 | 0.59213 | 0.0012817 | 52898.2158 | 0.023611 | 1.7 | 37.7381 | 44.0337 | 4.075 | 0.36751
2025-02-06 16:54 | 0.53202 | 0.60435 | 26.5053 | 0.055238 | 0.97853 | 0.5845 | 0.0012651 | 52216.1471 | 0.023611 | 1.7 | 37.3193 | 43.545 | 4.0174 | 0.36232
2025-02-06 16:55 | 0.54322 | 0.61707 | 26.5054 | 0.05515 | 0.97853 | 0.5968 | 0.0012918 | 53315.0392 | 0.023611 | 1.7 | 37.9937 | 44.3319 | 4.091 | 0.36895
2025-02-06 16:56 | 0.53588 | 0.60874 | 26.5057 | 0.055059 | 0.97853 | 0.58874 | 0.0012743 | 52595.164 | 0.023611 | 1.7 | 37.5521 | 43.8169 | 4.032 | 0.36363
2025-02-06 16:57 | 0.51812 | 0.58857 | 26.5061 | 0.055003 | 0.97853 | 0.56923 | 0.0012321 | 50852.2167 | 0.023611 | 1.7 | 36.4793 | 42.5656 | 3.9014 | 0.35186
2025-02-06 16:58 | 0.5216 | 0.59252 | 26.5065 | 0.054975 | 0.97853 | 0.57304 | 0.0012404 | 51193.3704 | 0.023611 | 1.7 | 36.6895 | 42.8114 | 3.9242 | 0.35392
2025-02-06 16:59 | 0.5131 | 0.58287 | 26.507 | 0.055114 | 0.97853 | 0.56371 | 0.0012202 | 50359.8415 | 0.02361 | 1.7001 | 36.1751 | 42.2116 | 3.8735 | 0.34934
2025-02-06 17:00 | 0.50885 | 0.57805 | 26.5074 | 0.055162 | 0.97853 | 0.55905 | 0.0012101 | 49943.1324 | 0.02361 | 1.7001 | 35.9175 | 41.9113 | 3.8465 | 0.3469
2025-02-06 17:01 | 0.51426 | 0.58419 | 26.5075 | 0.054987 | 0.97853 | 0.56499 | 0.0012229 | 50473.6724 | 0.02361 | 1.7001 | 36.2454 | 42.2941 | 3.8729 | 0.34928
2025-02-06 17:02 | 0.50268 | 0.57103 | 26.5075 | 0.054908 | 0.97853 | 0.55226 | 0.0011954 | 49336.8773 | 0.02361 | 1.7001 | 35.5422 | 41.4735 | 3.7847 | 0.34133
2025-02-06 17:03 | 0.4633 | 0.52629 | 26.5075 | 0.05486 | 0.97853 | 0.509 | 0.0011017 | 45471.7758 | 0.02361 | 1.7001 | 33.1341 | 38.6635 | 3.5 | 0.31566
2025-02-06 17:04 | 0.41542 | 0.47191 | 26.5075 | 0.054793 | 0.97853 | 0.4564 | 0.00098788 | 40773.0258 | 0.02361 | 1.7001 | 30.1674 | 35.2017 | 3.152 | 0.28427
2025-02-06 17:05 | 0.38415 | 0.43639 | 26.5075 | 0.054546 | 0.97853 | 0.42204 | 0.00091351 | 37703.6804 | 0.02361 | 1.7001 | 28.2037 | 32.9104 | 2.9131 | 0.26273
2025-02-06 17:06 | 0.38029 | 0.432 | 26.5075 | 0.054265 | 0.97853 | 0.4178 | 0.00090433 | 37324.749 | 0.02361 | 1.7001 | 27.9598 | 32.6258 | 2.8704 | 0.25888
2025-02-06 17:07 | 0.3745 | 0.42542 | 26.5075 | 0.054015 | 0.97853 | 0.41144 | 0.00089056 | 36756.3554 | 0.02361 | 1.7001 | 27.5932 | 32.198 | 2.8159 | 0.25396
2025-02-06 17:08 | 0.35712 | 0.40569 | 26.508 | 0.053396 | 0.97852 | 0.39235 | 0.00084924 | 35051.252 | 0.02361 | 1.7001 | 26.4887 | 30.9095 | 2.6608 | 0.23997
2025-02-06 17:09 | 0.38608 | 0.43858 | 26.5086 | 0.05251 | 0.97852 | 0.42416 | 0.0009181 | 37893.3781 | 0.023609 | 1.7001 | 28.3256 | 33.0535 | 2.8179 | 0.25414
2025-02-06 17:10 | 0.39033 | 0.44341 | 26.5093 | 0.051765 | 0.97852 | 0.42883 | 0.0009282 | 38310.3394 | 0.023609 | 1.7002 | 28.5933 | 33.3664 | 2.807 | 0.25315
2025-02-06 17:11 | 0.36987 | 0.42016 | 26.5099 | 0.051091 | 0.97852 | 0.40635 | 0.00087954 | 36302.1105 | 0.023608 | 1.7002 | 27.2994 | 31.857 | 2.6323 | 0.2374
2025-02-06 17:12 | 0.38106 | 0.43288 | 26.5105 | 0.050075 | 0.97852 | 0.41865 | 0.00090617 | 37401.1533 | 0.023608 | 1.7002 | 28.0086 | 32.6851 | 2.6542 | 0.23937
2025-02-06 17:13 | 0.38917 | 0.44209 | 26.5108 | 0.048819 | 0.97852 | 0.42756 | 0.00092545 | 38196.9805 | 0.023608 | 1.7002 | 28.5203 | 33.2825 | 2.6398 | 0.23808
2025-02-06 17:14 | 0.3911 | 0.44429 | 26.511 | 0.048418 | 0.97852 | 0.42968 | 0.00093004 | 38386.4823 | 0.023607 | 1.7002 | 28.642 | 33.4246 | 2.6305 | 0.23724
2025-02-06 17:15 | 0.3938 | 0.44736 | 26.5111 | 0.048129 | 0.97852 | 0.43265 | 0.00093646 | 38651.7726 | 0.023607 | 1.7002 | 28.8121 | 33.6232 | 2.632 | 0.23737
2025-02-06 17:16 | 0.38994 | 0.44297 | 26.5113 | 0.047957 | 0.97852 | 0.42841 | 0.00092728 | 38272.8658 | 0.023607 | 1.7003 | 28.569 | 33.3397 | 2.5982 | 0.23432
2025-02-06 17:17 | 0.38647 | 0.43903 | 26.5114 | 0.047539 | 0.97852 | 0.42459 | 0.00091902 | 37931.8515 | 0.023607 | 1.7003 | 28.3499 | 33.0841 | 2.5538 | 0.23032
2025-02-06 17:18 | 0.40075 | 0.45525 | 26.5116 | 0.04738 | 0.97852 | 0.44028 | 0.00095299 | 39333.9599 | 0.023607 | 1.7003 | 29.2488 | 34.1332 | 2.6345 | 0.2376
2025-02-06 17:19 | 0.42083 | 0.47806 | 26.5117 | 0.047373 | 0.97852 | 0.46234 | 0.0010007 | 41304.4788 | 0.023607 | 1.7003 | 30.5046 | 35.5989 | 2.7592 | 0.24885
2025-02-06 17:20 | 0.42623 | 0.4842 | 26.5115 | 0.047732 | 0.97852 | 0.46828 | 0.0010136 | 41834.9336 | 0.023607 | 1.7003 | 30.8413 | 35.9915 | 2.814 | 0.25378
2025-02-06 17:21 | 0.42623 | 0.4842 | 26.511 | 0.047831 | 0.97852 | 0.46828 | 0.0010136 | 41834.8358 | 0.023607 | 1.7002 | 30.8413 | 35.9911 | 2.8198 | 0.25431
2025-02-06 17:22 | 0.42816 | 0.48639 | 26.5106 | 0.047448 | 0.97852 | 0.4704 | 0.0010182 | 42024.2077 | 0.023608 | 1.7002 | 30.9613 | 36.1309 | 2.8092 | 0.25335
2025-02-06 17:23 | 0.42508 | 0.48288 | 26.5102 | 0.047391 | 0.97852 | 0.467 | 0.0010108 | 41720.9605 | 0.023608 | 1.7002 | 30.7692 | 35.9063 | 2.7865 | 0.25131
2025-02-06 17:24 | 0.40925 | 0.4649 | 26.5098 | 0.047848 | 0.97852 | 0.44961 | 0.00097319 | 40167.2296 | 0.023608 | 1.7002 | 29.7812 | 34.753 | 2.7139 | 0.24476
2025-02-06 17:25 | 0.40616 | 0.46139 | 26.5098 | 0.047685 | 0.97852 | 0.44622 | 0.00096584 | 39864.0804 | 0.023608 | 1.7002 | 29.5878 | 34.5273 | 2.6852 | 0.24218
2025-02-06 17:26 | 0.41118 | 0.46709 | 26.5099 | 0.04778 | 0.97852 | 0.45173 | 0.00097778 | 40356.7295 | 0.023608 | 1.7002 | 29.9019 | 34.894 | 2.7221 | 0.2455
2025-02-06 17:27 | 0.41079 | 0.46665 | 26.5101 | 0.047885 | 0.97852 | 0.45131 | 0.00097686 | 40318.87 | 0.023608 | 1.7002 | 29.8778 | 34.866 | 2.7257 | 0.24582
2025-02-06 17:28 | 0.42353 | 0.48113 | 26.5102 | 0.047906 | 0.97852 | 0.46531 | 0.0010072 | 41569.3962 | 0.023608 | 1.7002 | 30.673 | 35.7941 | 2.8071 | 0.25317
2025-02-06 17:29 | 0.42623 | 0.4842 | 26.5104 | 0.047704 | 0.97852 | 0.46828 | 0.0010136 | 41834.6854 | 0.023608 | 1.7002 | 30.8413 | 35.9906 | 2.8122 | 0.25362
2025-02-06 17:30 | 0.4243 | 0.48201 | 26.5105 | 0.047725 | 0.97852 | 0.46616 | 0.001009 | 41645.2524 | 0.023608 | 1.7002 | 30.7211 | 35.8505 | 2.8014 | 0.25265
2025-02-06 17:31 | 0.41774 | 0.47455 | 26.5107 | 0.047951 | 0.97852 | 0.45894 | 0.00099339 | 41001.0914 | 0.023608 | 1.7002 | 30.312 | 35.3732 | 2.7733 | 0.25012
2025-02-06 17:32 | 0.41813 | 0.47499 | 26.5107 | 0.048035 | 0.97852 | 0.45937 | 0.00099431 | 41038.9926 | 0.023608 | 1.7002 | 30.3361 | 35.4013 | 2.7806 | 0.25078
2025-02-06 17:33 | 0.42623 | 0.4842 | 26.5107 | 0.048083 | 0.97852 | 0.46828 | 0.0010136 | 41834.7631 | 0.023608 | 1.7002 | 30.8413 | 35.9909 | 2.8346 | 0.25564
2025-02-06 17:34 | 0.42623 | 0.4842 | 26.5107 | 0.048164 | 0.97852 | 0.46828 | 0.0010136 | 41834.7631 | 0.023608 | 1.7002 | 30.8413 | 35.9909 | 2.8393 | 0.25607
2025-02-06 17:35 | 0.42816 | 0.48639 | 26.5107 | 0.048419 | 0.97852 | 0.4704 | 0.0010182 | 42024.2328 | 0.023608 | 1.7002 | 30.9613 | 36.131 | 2.8666 | 0.25854
2025-02-06 17:36 | 0.42314 | 0.48069 | 26.5107 | 0.048209 | 0.97852 | 0.46488 | 0.0010062 | 41531.6133 | 0.023608 | 1.7002 | 30.649 | 35.7665 | 2.8225 | 0.25455
2025-02-06 17:37 | 0.41426 | 0.4706 | 26.5107 | 0.048323 | 0.97852 | 0.45513 | 0.00098512 | 40660.0549 | 0.023608 | 1.7002 | 30.095 | 35.12 | 2.7728 | 0.25007
2025-02-06 17:38 | 0.42276 | 0.48025 | 26.5107 | 0.048533 | 0.97852 | 0.46446 | 0.0010053 | 41493.7152 | 0.023608 | 1.7002 | 30.6249 | 35.7384 | 2.839 | 0.25604
2025-02-06 17:39 | 0.43087 | 0.48946 | 26.5102 | 0.048345 | 0.97852 | 0.47337 | 0.0010246 | 42289.3769 | 0.023608 | 1.7002 | 31.1293 | 36.3266 | 2.8794 | 0.25968
2025-02-06 17:40 | 0.42121 | 0.47849 | 26.5096 | 0.048414 | 0.97852 | 0.46276 | 0.0010016 | 41341.8894 | 0.023608 | 1.7002 | 30.5287 | 35.6251 | 2.8221 | 0.25452
2025-02-06 17:41 | 0.39998 | 0.45437 | 26.5089 | 0.048211 | 0.97852 | 0.43943 | 0.00095115 | 39257.6042 | 0.023609 | 1.7001 | 29.2004 | 34.0745 | 2.6756 | 0.2413
2025-02-06 17:42 | 0.38338 | 0.43551 | 26.5083 | 0.047831 | 0.97852 | 0.42119 | 0.00091168 | 37628.0543 | 0.023609 | 1.7001 | 28.155 | 32.8541 | 2.5497 | 0.22995
2025-02-06 17:43 | 0.37527 | 0.4263 | 26.5077 | 0.048076 | 0.97853 | 0.41229 | 0.0008924 | 36832.1745 | 0.02361 | 1.7001 | 27.6421 | 32.2553 | 2.5112 | 0.22648
2025-02-06 17:44 | 0.37913 | 0.43068 | 26.5077 | 0.04792 | 0.97853 | 0.41653 | 0.00090158 | 37211.1048 | 0.02361 | 1.7001 | 27.8865 | 32.5404 | 2.5275 | 0.22795
2025-02-06 17:45 | 0.38647 | 0.43902 | 26.5079 | 0.048041 | 0.97852 | 0.42459 | 0.00091902 | 37931.1178 | 0.02361 | 1.7001 | 28.3499 | 33.0813 | 2.5804 | 0.23272
2025-02-06 17:46 | 0.38724 | 0.4399 | 26.5081 | 0.047982 | 0.97852 | 0.42544 | 0.00092086 | 38006.948 | 0.02361 | 1.7001 | 28.3986 | 33.1383 | 2.5822 | 0.23288
2025-02-06 17:47 | 0.38647 | 0.43902 | 26.5083 | 0.047836 | 0.97852 | 0.42459 | 0.00091902 | 37931.2061 | 0.023609 | 1.7001 | 28.3499 | 33.0817 | 2.5695 | 0.23173
2025-02-06 17:48 | 0.3911 | 0.44428 | 26.5085 | 0.04787 | 0.97852 | 0.42968 | 0.00093004 | 38385.9645 | 0.023609 | 1.7001 | 28.642 | 33.4226 | 2.6006 | 0.23454
2025-02-06 17:49 | 0.3938 | 0.44735 | 26.5082 | 0.047812 | 0.97852 | 0.43265 | 0.00093646 | 38651.1634 | 0.023609 | 1.7001 | 28.8121 | 33.6209 | 2.6145 | 0.23579
2025-02-06 17:50 | 0.39187 | 0.44516 | 26.5078 | 0.047809 | 0.97852 | 0.43053 | 0.00093187 | 38461.6066 | 0.02361 | 1.7001 | 28.6906 | 33.4788 | 2.6021 | 0.23468
2025-02-06 17:51 | 0.38917 | 0.44209 | 26.5074 | 0.04786 | 0.97853 | 0.42756 | 0.00092545 | 38196.2642 | 0.02361 | 1.7001 | 28.5203 | 33.2798 | 2.5878 | 0.23338
2025-02-06 17:52 | 0.38917 | 0.44209 | 26.5069 | 0.047725 | 0.97853 | 0.42756 | 0.00092545 | 38196.1753 | 0.02361 | 1.7001 | 28.5203 | 33.2794 | 2.5804 | 0.23272
2025-02-06 17:53 | 0.3911 | 0.44428 | 26.5065 | 0.047642 | 0.97853 | 0.42968 | 0.00093004 | 38385.55 | 0.023611 | 1.7 | 28.642 | 33.421 | 2.588 | 0.23341
2025-02-06 17:54 | 0.38994 | 0.44296 | 26.5059 | 0.047508 | 0.97853 | 0.42841 | 0.00092728 | 38271.7499 | 0.023611 | 1.7 | 28.569 | 33.3354 | 2.5734 | 0.23209
2025-02-06 17:55 | 0.38454 | 0.43682 | 26.5053 | 0.047547 | 0.97853 | 0.42247 | 0.00091443 | 37741.1187 | 0.023612 | 1.7 | 28.2281 | 32.9371 | 2.5416 | 0.22922
2025-02-06 17:56 | 0.38454 | 0.43682 | 26.5046 | 0.047281 | 0.97853 | 0.42247 | 0.00091443 | 37740.9864 | 0.023612 | 1.7 | 28.2281 | 32.9366 | 2.5273 | 0.22793
2025-02-06 17:57 | 0.38068 | 0.43243 | 26.504 | 0.047242 | 0.97853 | 0.41823 | 0.00090525 | 37361.9303 | 0.023612 | 1.6999 | 27.9842 | 32.6515 | 2.5011 | 0.22557
2025-02-06 17:58 | 0.38106 | 0.43287 | 26.5034 | 0.047329 | 0.97853 | 0.41865 | 0.00090617 | 37399.6966 | 0.023613 | 1.6999 | 28.0086 | 32.6795 | 2.5081 | 0.2262
2025-02-06 17:59 | 0.38917 | 0.44208 | 26.5032 | 0.047211 | 0.97853 | 0.42756 | 0.00092545 | 38195.4001 | 0.023613 | 1.6999 | 28.5203 | 33.2765 | 2.5524 | 0.23019
2025-02-06 18:00 | 0.38724 | 0.43988 | 26.5032 | 0.047237 | 0.97853 | 0.42544 | 0.00092086 | 38005.9398 | 0.023613 | 1.6999 | 28.3986 | 33.1345 | 2.5417 | 0.22923
2025-02-06 18:01 | 0.38454 | 0.43681 | 26.5032 | 0.047323 | 0.97853 | 0.42247 | 0.00091443 | 37740.6955 | 0.023613 | 1.6999 | 28.2281 | 32.9355 | 2.5295 | 0.22813
2025-02-06 18:02 | 0.38647 | 0.43901 | 26.5032 | 0.047146 | 0.97853 | 0.42459 | 0.00091902 | 37930.1557 | 0.023613 | 1.6999 | 28.3499 | 33.0777 | 2.532 | 0.22836
2025-02-06 18:03 | 0.3911 | 0.44427 | 26.5032 | 0.047002 | 0.97853 | 0.42968 | 0.00093004 | 38384.8621 | 0.023613 | 1.6999 | 28.642 | 33.4184 | 2.553 | 0.23025
2025-02-06 18:04 | 0.3938 | 0.44734 | 26.5032 | 0.046936 | 0.97853 | 0.43265 | 0.00093646 | 38650.109 | 0.023613 | 1.6999 | 28.8121 | 33.6169 | 2.5662 | 0.23144
2025-02-06 18:05 | 0.39959 | 0.45392 | 26.5032 | 0.046847 | 0.97853 | 0.43901 | 0.00095024 | 39218.4852 | 0.023613 | 1.6999 | 29.1761 | 34.0416 | 2.597 | 0.23422
2025-02-06 18:06 | 0.40191 | 0.45655 | 26.5025 | 0.046774 | 0.97854 | 0.44155 | 0.00095574 | 39445.7 | 0.023613 | 1.6999 | 29.3215 | 34.2107 | 2.6072 | 0.23514
2025-02-06 18:07 | 0.39959 | 0.45391 | 26.5017 | 0.046827 | 0.97854 | 0.43901 | 0.00095024 | 39218.1645 | 0.023614 | 1.6998 | 29.1761 | 34.0404 | 2.5958 | 0.23411
2025-02-06 18:08 | 0.40577 | 0.46093 | 26.5008 | 0.04672 | 0.97854 | 0.4458 | 0.00096493 | 39824.2499 | 0.023615 | 1.6998 | 29.5636 | 34.4917 | 2.6278 | 0.237
2025-02-06 18:09 | 0.405 | 0.46005 | 26.4999 | 0.046194 | 0.97854 | 0.44495 | 0.00096309 | 39748.281 | 0.023615 | 1.6997 | 29.5152 | 34.4346 | 2.5935 | 0.2339
2025-02-06 18:10 | 0.40384 | 0.45873 | 26.4991 | 0.046206 | 0.97854 | 0.44367 | 0.00096034 | 39634.4312 | 0.023616 | 1.6997 | 29.4426 | 34.3492 | 2.5871 | 0.23332
2025-02-06 18:11 | 0.40037 | 0.45478 | 26.4989 | 0.046203 | 0.97854 | 0.43986 | 0.00095207 | 39293.363 | 0.023616 | 1.6997 | 29.2246 | 34.0947 | 2.5657 | 0.2314
2025-02-06 18:12 | 0.39921 | 0.45347 | 26.4989 | 0.046016 | 0.97854 | 0.43858 | 0.00094932 | 39179.6877 | 0.023616 | 1.6997 | 29.1519 | 34.0099 | 2.5483 | 0.22982
2025-02-06 18:13 | 0.39766 | 0.45171 | 26.4989 | 0.045732 | 0.97854 | 0.43689 | 0.00094565 | 39028.1224 | 0.023616 | 1.6997 | 29.0549 | 33.8967 | 2.5233 | 0.22757
2025-02-06 18:14 | 0.405 | 0.46005 | 26.4989 | 0.045854 | 0.97854 | 0.44495 | 0.00096309 | 39748.0588 | 0.023616 | 1.6997 | 29.5152 | 34.4337 | 2.5743 | 0.23217
2025-02-06 18:15 | 0.4077 | 0.46312 | 26.4989 | 0.045904 | 0.97854 | 0.44792 | 0.00096952 | 40013.2995 | 0.023616 | 1.6997 | 29.6845 | 34.6313 | 2.5934 | 0.23389
2025-02-06 18:16 | 0.41156 | 0.4675 | 26.4989 | 0.046201 | 0.97854 | 0.45216 | 0.0009787 | 40392.2129 | 0.023616 | 1.6997 | 29.9261 | 34.9131 | 2.6337 | 0.23753
2025-02-06 18:17 | 0.41311 | 0.46926 | 26.4989 | 0.046118 | 0.97854 | 0.45385 | 0.00098237 | 40543.7733 | 0.023616 | 1.6997 | 30.0226 | 35.0257 | 2.6383 | 0.23794
2025-02-06 18:18 | 0.40963 | 0.46531 | 26.4985 | 0.045957 | 0.97854 | 0.45004 | 0.00097411 | 40202.6734 | 0.023616 | 1.6997 | 29.8053 | 34.7719 | 2.6081 | 0.23522
2025-02-06 18:19 | 0.41426 | 0.47057 | 26.4981 | 0.046124 | 0.97854 | 0.45513 | 0.00098512 | 40657.2668 | 0.023617 | 1.6997 | 30.095 | 35.1095 | 2.6456 | 0.2386
2025-02-06 18:20 | 0.41311 | 0.46925 | 26.4976 | 0.046064 | 0.97855 | 0.45385 | 0.00098237 | 40543.4933 | 0.023617 | 1.6996 | 30.0226 | 35.0247 | 2.6351 | 0.23766
2025-02-06 18:21 | 0.41542 | 0.47188 | 26.4972 | 0.046088 | 0.97855 | 0.4564 | 0.00098788 | 40770.738 | 0.023617 | 1.6996 | 30.1674 | 35.1931 | 2.6505 | 0.23904
2025-02-06 18:22 | 0.42237 | 0.47978 | 26.4967 | 0.045951 | 0.97855 | 0.46403 | 0.0010044 | 41452.6723 | 0.023618 | 1.6996 | 30.6009 | 35.6984 | 2.6845 | 0.24211
2025-02-06 18:23 | 0.42083 | 0.47802 | 26.4962 | 0.046076 | 0.97855 | 0.46234 | 0.0010007 | 41301.0057 | 0.023618 | 1.6996 | 30.5046 | 35.5858 | 2.6825 | 0.24193
2025-02-06 18:24 | 0.42623 | 0.48416 | 26.4958 | 0.045963 | 0.97855 | 0.46828 | 0.0010136 | 41831.3742 | 0.023618 | 1.6996 | 30.8413 | 35.9781 | 2.7084 | 0.24427
2025-02-06 18:25 | 0.42816 | 0.48635 | 26.4954 | 0.045933 | 0.97855 | 0.4704 | 0.0010182 | 42020.7505 | 0.023618 | 1.6995 | 30.9613 | 36.1179 | 2.7183 | 0.24516
2025-02-06 18:26 | 0.42894 | 0.48723 | 26.4951 | 0.045874 | 0.97855 | 0.47125 | 0.00102 | 42096.4621 | 0.023619 | 1.6995 | 31.0094 | 36.1737 | 2.7194 | 0.24525
2025-02-06 18:27 | 0.42623 | 0.48416 | 26.4948 | 0.045707 | 0.97855 | 0.46828 | 0.0010136 | 41831.1573 | 0.023619 | 1.6995 | 30.8413 | 35.9773 | 2.6933 | 0.2429
2025-02-06 18:28 | 0.4243 | 0.48196 | 26.4945 | 0.04557 | 0.97855 | 0.46616 | 0.001009 | 41641.6364 | 0.023619 | 1.6995 | 30.7211 | 35.8369 | 2.6736 | 0.24113
2025-02-06 18:29 | 0.42353 | 0.48109 | 26.4942 | 0.045516 | 0.97855 | 0.46531 | 0.0010072 | 41565.7868 | 0.023619 | 1.6995 | 30.673 | 35.7805 | 2.6658 | 0.24043
2025-02-06 18:30 | 0.42623 | 0.48415 | 26.4939 | 0.045486 | 0.97855 | 0.46828 | 0.0010136 | 41830.9486 | 0.023619 | 1.6995 | 30.8413 | 35.9765 | 2.6802 | 0.24172
2025-02-06 18:31 | 0.41658 | 0.47319 | 26.4936 | 0.045367 | 0.97855 | 0.45767 | 0.00099063 | 40883.618 | 0.02362 | 1.6995 | 30.2397 | 35.2745 | 2.6157 | 0.2359
2025-02-06 18:32 | 0.40307 | 0.45784 | 26.493 | 0.045456 | 0.97855 | 0.44283 | 0.0009585 | 39557.3364 | 0.02362 | 1.6994 | 29.3942 | 34.2877 | 2.54 | 0.22908
2025-02-06 18:33 | 0.41272 | 0.4688 | 26.4924 | 0.045338 | 0.97856 | 0.45343 | 0.00098145 | 40504.4487 | 0.023621 | 1.6994 | 29.9985 | 34.9922 | 2.5909 | 0.23367
2025-02-06 18:34 | 0.42816 | 0.48634 | 26.4917 | 0.045505 | 0.97856 | 0.4704 | 0.0010182 | 42019.9037 | 0.023621 | 1.6994 | 30.9613 | 36.1147 | 2.6926 | 0.24284
2025-02-06 18:35 | 0.42894 | 0.48722 | 26.4911 | 0.045444 | 0.97856 | 0.47125 | 0.00102 | 42095.5364 | 0.023621 | 1.6993 | 31.0094 | 36.1702 | 2.6936 | 0.24293
2025-02-06 18:36 | 0.4243 | 0.48195 | 26.4905 | 0.045467 | 0.97856 | 0.46616 | 0.001009 | 41640.7214 | 0.023622 | 1.6993 | 30.7211 | 35.8334 | 2.6673 | 0.24056
2025-02-06 18:37 | 0.42353 | 0.48108 | 26.4903 | 0.045293 | 0.97856 | 0.46531 | 0.0010072 | 41564.9102 | 0.023622 | 1.6993 | 30.673 | 35.7772 | 2.6525 | 0.23922
2025-02-06 18:38 | 0.42623 | 0.48415 | 26.4903 | 0.045236 | 0.97856 | 0.46828 | 0.0010136 | 41830.136 | 0.023622 | 1.6993 | 30.8413 | 35.9735 | 2.6652 | 0.24037
2025-02-06 18:39 | 0.42623 | 0.48415 | 26.4903 | 0.045241 | 0.97856 | 0.46828 | 0.0010136 | 41830.136 | 0.023622 | 1.6993 | 30.8413 | 35.9735 | 2.6655 | 0.24039
2025-02-06 18:40 | 0.42623 | 0.48415 | 26.4903 | 0.045097 | 0.97856 | 0.46828 | 0.0010136 | 41830.136 | 0.023622 | 1.6993 | 30.8413 | 35.9735 | 2.657 | 0.23963
2025-02-06 18:41 | 0.42623 | 0.48415 | 26.4903 | 0.045051 | 0.97856 | 0.46828 | 0.0010136 | 41830.136 | 0.023622 | 1.6993 | 30.8413 | 35.9735 | 2.6543 | 0.23939
2025-02-06 18:42 | 0.42237 | 0.47976 | 26.4903 | 0.045105 | 0.97856 | 0.46403 | 0.0010044 | 41451.2402 | 0.023622 | 1.6993 | 30.6009 | 35.6931 | 2.6346 | 0.23761
2025-02-06 18:43 | 0.41504 | 0.47143 | 26.4903 | 0.045032 | 0.97856 | 0.45598 | 0.00098696 | 40731.3346 | 0.023622 | 1.6993 | 30.1432 | 35.1593 | 2.5869 | 0.23331
2025-02-06 18:44 | 0.41426 | 0.47055 | 26.4901 | 0.044968 | 0.97856 | 0.45513 | 0.00098512 | 40655.5183 | 0.023622 | 1.6993 | 30.095 | 35.1029 | 2.5787 | 0.23257
2025-02-06 18:45 | 0.42083 | 0.478 | 26.4899 | 0.045083 | 0.97856 | 0.46234 | 0.0010007 | 41299.5937 | 0.023622 | 1.6993 | 30.5046 | 35.5805 | 2.6242 | 0.23667
2025-02-06 18:46 | 0.42237 | 0.47976 | 26.4897 | 0.045156 | 0.97856 | 0.46403 | 0.0010044 | 41451.1034 | 0.023622 | 1.6993 | 30.6009 | 35.6925 | 2.6376 | 0.23788
2025-02-06 18:47 | 0.41118 | 0.46704 | 26.4895 | 0.044893 | 0.97856 | 0.45173 | 0.00097778 | 40352.2612 | 0.023623 | 1.6993 | 29.9019 | 34.8772 | 2.5562 | 0.23053
2025-02-06 18:48 | 0.40307 | 0.45783 | 26.4893 | 0.04491 | 0.97856 | 0.44283 | 0.0009585 | 39556.5311 | 0.023623 | 1.6993 | 29.3942 | 34.2847 | 2.5092 | 0.2263
2025-02-06 18:49 | 0.405 | 0.46002 | 26.4887 | 0.04504 | 0.97856 | 0.44495 | 0.00096309 | 39745.8606 | 0.023623 | 1.6992 | 29.5152 | 34.4254 | 2.5278 | 0.22798
2025-02-06 18:50 | 0.41156 | 0.46747 | 26.4881 | 0.044948 | 0.97857 | 0.45216 | 0.0009787 | 40389.8381 | 0.023624 | 1.6992 | 29.9261 | 34.9041 | 2.5615 | 0.23101
2025-02-06 18:51 | 0.41311 | 0.46923 | 26.4874 | 0.044851 | 0.97857 | 0.45385 | 0.00098237 | 40541.253 | 0.023624 | 1.6992 | 30.0226 | 35.0162 | 2.565 | 0.23133
2025-02-06 18:52 | 0.39998 | 0.45432 | 26.4868 | 0.044647 | 0.97857 | 0.43943 | 0.00095115 | 39252.8887 | 0.023625 | 1.6992 | 29.2004 | 34.0566 | 2.4762 | 0.22332
2025-02-06 18:53 | 0.39303 | 0.44642 | 26.4862 | 0.044903 | 0.97857 | 0.4318 | 0.00093463 | 38570.7564 | 0.023625 | 1.6991 | 28.7635 | 33.5466 | 2.4492 | 0.22089
2025-02-06 18:54 | 0.39071 | 0.44379 | 26.4857 | 0.04492 | 0.97857 | 0.42925 | 0.00092912 | 38343.3254 | 0.023625 | 1.6991 | 28.6177 | 33.3761 | 2.4364 | 0.21973
2025-02-06 18:55 | 0.37604 | 0.42712 | 26.4852 | 0.044569 | 0.97857 | 0.41314 | 0.00089423 | 36903.469 | 0.023626 | 1.6991 | 27.6911 | 32.2951 | 2.331 | 0.21023
2025-02-06 18:56 | 0.36871 | 0.41879 | 26.4848 | 0.044432 | 0.97857 | 0.40508 | 0.00087679 | 36183.5022 | 0.023626 | 1.6991 | 27.2259 | 31.7523 | 2.2807 | 0.20569
2025-02-06 18:57 | 0.37373 | 0.42449 | 26.4844 | 0.044844 | 0.97857 | 0.41059 | 0.00088872 | 36675.9673 | 0.023626 | 1.699 | 27.5443 | 32.1233 | 2.3316 | 0.21028
2025-02-06 18:58 | 0.38068 | 0.43238 | 26.4839 | 0.044761 | 0.97857 | 0.41823 | 0.00090525 | 37357.8638 | 0.023627 | 1.699 | 27.9842 | 32.636 | 2.3684 | 0.2136
2025-02-06 18:59 | 0.37141 | 0.42186 | 26.483 | 0.044705 | 0.97858 | 0.40805 | 0.00088321 | 36448.3593 | 0.023627 | 1.699 | 27.3974 | 31.9509 | 2.3106 | 0.20839
2025-02-06 19:00 | 0.37566 | 0.42668 | 26.4819 | 0.044672 | 0.97858 | 0.41271 | 0.00089331 | 36864.9122 | 0.023628 | 1.6989 | 27.6666 | 32.2641 | 2.3339 | 0.21049
2025-02-06 19:01 | 0.37566 | 0.42667 | 26.4808 | 0.044529 | 0.97858 | 0.41271 | 0.00089331 | 36864.6967 | 0.023629 | 1.6989 | 27.6666 | 32.2632 | 2.3264 | 0.20981
2025-02-06 19:02 | 0.34709 | 0.39422 | 26.4798 | 0.044482 | 0.97858 | 0.38132 | 0.00082537 | 34060.8118 | 0.023629 | 1.6988 | 25.8471 | 30.1407 | 2.1556 | 0.1944
2025-02-06 19:03 | 0.3413 | 0.38764 | 26.4787 | 0.044325 | 0.97858 | 0.37496 | 0.0008116 | 33492.3053 | 0.02363 | 1.6988 | 25.4758 | 29.7069 | 2.1138 | 0.19064
2025-02-06 19:04 | 0.35211 | 0.39992 | 26.4776 | 0.044253 | 0.97859 | 0.38684 | 0.00083731 | 34552.9468 | 0.023631 | 1.6987 | 26.1682 | 30.5136 | 2.1738 | 0.19605
2025-02-06 19:05 | 0.35211 | 0.39992 | 26.4766 | 0.04431 | 0.97859 | 0.38684 | 0.00083731 | 34552.7653 | 0.023632 | 1.6987 | 26.1682 | 30.5129 | 2.1765 | 0.1963
2025-02-06 19:06 | 0.35983 | 0.40869 | 26.4769 | 0.044104 | 0.97859 | 0.39532 | 0.00085567 | 35310.5555 | 0.023631 | 1.6987 | 26.661 | 31.0877 | 2.2116 | 0.19946
2025-02-06 19:07 | 0.37064 | 0.42097 | 26.4776 | 0.044051 | 0.97859 | 0.4072 | 0.00088138 | 36371.5149 | 0.023631 | 1.6987 | 27.3484 | 31.8897 | 2.2719 | 0.2049
2025-02-06 19:08 | 0.38415 | 0.43632 | 26.4782 | 0.044151 | 0.97859 | 0.42204 | 0.00091351 | 37697.6911 | 0.023631 | 1.6988 | 28.2037 | 32.8876 | 2.3559 | 0.21248
2025-02-06 19:09 | 0.40307 | 0.4578 | 26.4789 | 0.044312 | 0.97858 | 0.44283 | 0.0009585 | 39554.2979 | 0.02363 | 1.6988 | 29.3942 | 34.2762 | 2.4751 | 0.22322
2025-02-06 19:10 | 0.42044 | 0.47754 | 26.4794 | 0.044166 | 0.97858 | 0.46191 | 0.00099981 | 41259.3463 | 0.02363 | 1.6988 | 30.4805 | 35.5435 | 2.5677 | 0.23158
2025-02-06 19:11 | 0.44283 | 0.50297 | 26.4787 | 0.044018 | 0.97858 | 0.48652 | 0.0010531 | 43456.6464 | 0.02363 | 1.6988 | 31.8716 | 37.1649 | 2.6882 | 0.24245
2025-02-06 19:12 | 0.43627 | 0.49551 | 26.4776 | 0.044056 | 0.97859 | 0.4793 | 0.0010375 | 42812.3129 | 0.023631 | 1.6987 | 31.4649 | 36.6898 | 2.6526 | 0.23923
2025-02-06 19:13 | 0.42894 | 0.48718 | 26.4765 | 0.043994 | 0.97859 | 0.47125 | 0.00102 | 42092.2138 | 0.023632 | 1.6987 | 31.0094 | 36.1577 | 2.6065 | 0.23508
2025-02-06 19:14 | 0.41658 | 0.47314 | 26.4755 | 0.043956 | 0.97859 | 0.45767 | 0.00099063 | 40879.5971 | 0.023632 | 1.6986 | 30.2397 | 35.2593 | 2.533 | 0.22844
2025-02-06 19:15 | 0.39535 | 0.44902 | 26.4744 | 0.043812 | 0.97859 | 0.43434 | 0.00094014 | 38795.6166 | 0.023633 | 1.6986 | 28.9092 | 33.7072 | 2.4023 | 0.21666
2025-02-06 19:16 | 0.37875 | 0.43017 | 26.4737 | 0.043793 | 0.97859 | 0.4161 | 0.00090066 | 37166.3572 | 0.023634 | 1.6986 | 27.8621 | 32.4857 | 2.3053 | 0.20791
2025-02-06 19:17 | 0.38222 | 0.43411 | 26.473 | 0.04375 | 0.9786 | 0.41992 | 0.00090892 | 37507.2023 | 0.023634 | 1.6985 | 28.0818 | 32.7414 | 2.3231 | 0.20952
2025-02-06 19:18 | 0.41581 | 0.47226 | 26.4724 | 0.043579 | 0.9786 | 0.45682 | 0.0009888 | 40803.1475 | 0.023635 | 1.6985 | 30.1915 | 35.2006 | 2.5066 | 0.22607
2025-02-06 19:19 | 0.42662 | 0.48453 | 26.4717 | 0.043722 | 0.9786 | 0.4687 | 0.0010145 | 41863.8068 | 0.023635 | 1.6985 | 30.8653 | 35.9856 | 2.5768 | 0.2324
2025-02-06 19:20 | 0.40384 | 0.45866 | 26.4711 | 0.043514 | 0.9786 | 0.44367 | 0.00096034 | 39628.4012 | 0.023636 | 1.6984 | 29.4426 | 34.3264 | 2.4344 | 0.21955
2025-02-06 19:21 | 0.38685 | 0.43937 | 26.4701 | 0.043364 | 0.9786 | 0.42501 | 0.00091994 | 37961.2287 | 0.023636 | 1.6984 | 28.3743 | 33.0801 | 2.3289 | 0.21004
2025-02-06 19:22 | 0.38029 | 0.43191 | 26.469 | 0.0433 | 0.9786 | 0.4178 | 0.00090433 | 37316.9577 | 0.023637 | 1.6984 | 27.9598 | 32.596 | 2.2879 | 0.20634
2025-02-06 19:23 | 0.38608 | 0.43848 | 26.4679 | 0.043412 | 0.97861 | 0.42416 | 0.0009181 | 37885.0165 | 0.023638 | 1.6983 | 28.3256 | 33.0216 | 2.3269 | 0.20986
2025-02-06 19:24 | 0.40616 | 0.46128 | 26.4669 | 0.043498 | 0.97861 | 0.44622 | 0.00096584 | 39854.8054 | 0.023639 | 1.6983 | 29.5878 | 34.4922 | 2.4464 | 0.22063
2025-02-06 19:25 | 0.44747 | 0.5082 | 26.4659 | 0.043529 | 0.97861 | 0.49161 | 0.0010641 | 43908.2498 | 0.023639 | 1.6982 | 32.1581 | 37.4877 | 2.6838 | 0.24204
2025-02-06 19:26 | 0.41967 | 0.47663 | 26.4662 | 0.043592 | 0.97861 | 0.46107 | 0.00099798 | 41180.6274 | 0.023639 | 1.6982 | 30.4324 | 35.4763 | 2.529 | 0.22808
2025-02-06 19:27 | 0.39419 | 0.44769 | 26.4669 | 0.043383 | 0.97861 | 0.43307 | 0.00093738 | 38680.3748 | 0.023639 | 1.6983 | 28.8364 | 33.6162 | 2.3716 | 0.21389
2025-02-06 19:28 | 0.42314 | 0.48058 | 26.4675 | 0.043328 | 0.97861 | 0.46488 | 0.0010062 | 41521.8801 | 0.023638 | 1.6983 | 30.649 | 35.7298 | 2.5336 | 0.2285
2025-02-06 19:29 | 0.44477 | 0.50513 | 26.4681 | 0.04336 | 0.97861 | 0.48864 | 0.0010577 | 43643.5894 | 0.023638 | 1.6983 | 31.991 | 37.2949 | 2.6582 | 0.23974
2025-02-06 19:30 | 0.41967 | 0.47663 | 26.4687 | 0.043334 | 0.9786 | 0.46107 | 0.00099798 | 41181.1837 | 0.023637 | 1.6983 | 30.4324 | 35.4784 | 2.5142 | 0.22675
2025-02-06 19:31 | 0.39226 | 0.4455 | 26.4683 | 0.043199 | 0.97861 | 0.43095 | 0.00093279 | 38491.2517 | 0.023638 | 1.6983 | 28.7149 | 33.4758 | 2.3506 | 0.212
2025-02-06 19:32 | 0.40307 | 0.45778 | 26.4677 | 0.043239 | 0.97861 | 0.44283 | 0.0009585 | 39551.8951 | 0.023638 | 1.6983 | 29.3942 | 34.2671 | 2.4144 | 0.21775
2025-02-06 19:33 | 0.38183 | 0.43366 | 26.467 | 0.043359 | 0.97861 | 0.4195 | 0.000908 | 37468.0917 | 0.023638 | 1.6983 | 28.0574 | 32.7083 | 2.2997 | 0.2074
2025-02-06 19:34 | 0.35404 | 0.40209 | 26.4664 | 0.043355 | 0.97861 | 0.38896 | 0.0008419 | 34740.2631 | 0.023639 | 1.6982 | 26.2916 | 30.6492 | 2.1401 | 0.19301
2025-02-06 19:35 | 0.3606 | 0.40954 | 26.4658 | 0.043146 | 0.97861 | 0.39617 | 0.00085751 | 35384.1843 | 0.023639 | 1.6982 | 26.7102 | 31.1368 | 2.1673 | 0.19546
2025-02-06 19:36 | 0.3718 | 0.42225 | 26.4654 | 0.04328 | 0.97861 | 0.40847 | 0.00088413 | 36482.7636 | 0.02364 | 1.6982 | 27.4219 | 31.9662 | 2.238 | 0.20184
2025-02-06 19:37 | 0.38183 | 0.43365 | 26.4651 | 0.04323 | 0.97861 | 0.4195 | 0.000908 | 37467.6981 | 0.02364 | 1.6982 | 28.0574 | 32.7068 | 2.2927 | 0.20678
2025-02-06 19:38 | 0.39805 | 0.45207 | 26.4648 | 0.043236 | 0.97861 | 0.43731 | 0.00094656 | 39058.7797 | 0.02364 | 1.6982 | 29.0791 | 33.8975 | 2.3854 | 0.21514
2025-02-06 19:39 | 0.40732 | 0.46259 | 26.4645 | 0.043308 | 0.97861 | 0.44749 | 0.0009686 | 39967.9375 | 0.02364 | 1.6981 | 29.6603 | 34.5748 | 2.4421 | 0.22025
2025-02-06 19:40 | 0.38222 | 0.43409 | 26.4642 | 0.043317 | 0.97861 | 0.41992 | 0.00090892 | 37505.3958 | 0.02364 | 1.6981 | 28.0818 | 32.7345 | 2.2995 | 0.20738
2025-02-06 19:41 | 0.36214 | 0.41129 | 26.4638 | 0.043279 | 0.97861 | 0.39787 | 0.00086118 | 35535.356 | 0.023641 | 1.6981 | 26.8085 | 31.25 | 2.1826 | 0.19685
2025-02-06 19:42 | 0.35674 | 0.40515 | 26.4635 | 0.043115 | 0.97862 | 0.39193 | 0.00084833 | 35004.914 | 0.023641 | 1.6981 | 26.4641 | 30.8483 | 2.1435 | 0.19332
2025-02-06 19:43 | 0.36446 | 0.41392 | 26.4629 | 0.043142 | 0.97862 | 0.40041 | 0.00086669 | 35762.4844 | 0.023641 | 1.6981 | 26.956 | 31.4212 | 2.1889 | 0.19741
2025-02-06 19:44 | 0.36755 | 0.41742 | 26.4623 | 0.043074 | 0.97862 | 0.4038 | 0.00087403 | 36065.4305 | 0.023642 | 1.6981 | 27.1523 | 31.6496 | 2.203 | 0.19869
2025-02-06 19:45 | 0.37411 | 0.42488 | 26.4616 | 0.043181 | 0.97862 | 0.41101 | 0.00088964 | 36709.3271 | 0.023642 | 1.698 | 27.5688 | 32.1345 | 2.2459 | 0.20255
2025-02-06 19:46 | 0.40616 | 0.46127 | 26.461 | 0.043106 | 0.97862 | 0.44622 | 0.00096584 | 39853.5373 | 0.023643 | 1.698 | 29.5878 | 34.4874 | 2.4239 | 0.21861
2025-02-06 19:47 | 0.40539 | 0.46039 | 26.4604 | 0.043174 | 0.97862 | 0.44537 | 0.00096401 | 39777.6291 | 0.023643 | 1.698 | 29.5394 | 34.4305 | 2.4233 | 0.21855
2025-02-06 19:48 | 0.38724 | 0.43978 | 26.4597 | 0.043185 | 0.97862 | 0.42544 | 0.00092086 | 37996.974 | 0.023644 | 1.6979 | 28.3986 | 33.1003 | 2.3208 | 0.20931
2025-02-06 19:49 | 0.39033 | 0.44329 | 26.4591 | 0.043046 | 0.97862 | 0.42883 | 0.0009282 | 38299.9087 | 0.023644 | 1.6979 | 28.5933 | 33.3267 | 2.3308 | 0.21021
2025-02-06 19:50 | 0.39651 | 0.4503 | 26.4584 | 0.04307 | 0.97863 | 0.43562 | 0.00094289 | 38905.9037 | 0.023644 | 1.6979 | 28.9821 | 33.7793 | 2.3671 | 0.21348
2025-02-06 19:51 | 0.38415 | 0.43627 | 26.4578 | 0.043241 | 0.97863 | 0.42204 | 0.00091351 | 37693.5132 | 0.023645 | 1.6978 | 28.2037 | 32.8716 | 2.306 | 0.20798
2025-02-06 19:52 | 0.36485 | 0.41434 | 26.4571 | 0.04317 | 0.97863 | 0.40083 | 0.00086761 | 35799.2396 | 0.023645 | 1.6978 | 26.9805 | 31.4455 | 2.1921 | 0.1977
2025-02-06 19:53 | 0.36253 | 0.41171 | 26.4564 | 0.042907 | 0.97863 | 0.39829 | 0.0008621 | 35571.7991 | 0.023646 | 1.6978 | 26.8331 | 31.2731 | 2.1656 | 0.19531
2025-02-06 19:54 | 0.37836 | 0.42969 | 26.4556 | 0.042891 | 0.97863 | 0.41568 | 0.00089974 | 37124.833 | 0.023646 | 1.6978 | 27.8377 | 32.4433 | 2.2545 | 0.20333
2025-02-06 19:55 | 0.38145 | 0.43319 | 26.4548 | 0.043046 | 0.97863 | 0.41907 | 0.00090709 | 37427.737 | 0.023647 | 1.6977 | 28.033 | 32.6704 | 2.2801 | 0.20564
2025-02-06 19:56 | 0.37257 | 0.42311 | 26.4541 | 0.042828 | 0.97863 | 0.40932 | 0.00088597 | 36556.2934 | 0.023648 | 1.6977 | 27.4709 | 32.0147 | 2.2183 | 0.20006
2025-02-06 19:57 | 0.38492 | 0.43713 | 26.4533 | 0.042812 | 0.97864 | 0.42289 | 0.00091535 | 37768.3669 | 0.023648 | 1.6976 | 28.2525 | 32.925 | 2.2872 | 0.20628
2025-02-06 19:58 | 0.38878 | 0.44152 | 26.4525 | 0.042732 | 0.97864 | 0.42713 | 0.00092453 | 38147.0286 | 0.023649 | 1.6976 | 28.496 | 33.2082 | 2.3047 | 0.20785
2025-02-06 19:59 | 0.37527 | 0.42617 | 26.4519 | 0.042852 | 0.97864 | 0.41229 | 0.0008924 | 36821.025 | 0.023649 | 1.6976 | 27.6421 | 32.2126 | 2.2347 | 0.20154
2025-02-06 20:00 | 0.37913 | 0.43055 | 26.4518 | 0.042939 | 0.97864 | 0.41653 | 0.00090158 | 37199.8398 | 0.023649 | 1.6976 | 27.8865 | 32.4974 | 2.2611 | 0.20393
2025-02-06 20:01 | 0.38647 | 0.43888 | 26.452 | 0.042848 | 0.97864 | 0.42459 | 0.00091902 | 37919.6222 | 0.023649 | 1.6976 | 28.3499 | 33.0375 | 2.2978 | 0.20723
2025-02-06 20:02 | 0.38724 | 0.43976 | 26.4521 | 0.04302 | 0.97864 | 0.42544 | 0.00092086 | 37995.4169 | 0.023649 | 1.6976 | 28.3986 | 33.0944 | 2.3114 | 0.20846
2025-02-06 20:03 | 0.37488 | 0.42573 | 26.4523 | 0.043024 | 0.97864 | 0.41186 | 0.00089148 | 36783.2323 | 0.023649 | 1.6976 | 27.6177 | 32.1844 | 2.2415 | 0.20215
2025-02-06 20:04 | 0.36523 | 0.41477 | 26.4525 | 0.04278 | 0.97864 | 0.40126 | 0.00086853 | 35836.2167 | 0.023649 | 1.6976 | 27.0051 | 31.4706 | 2.1743 | 0.19609
2025-02-06 20:05 | 0.3745 | 0.42529 | 26.4526 | 0.042642 | 0.97864 | 0.41144 | 0.00089056 | 36745.4104 | 0.023649 | 1.6976 | 27.5932 | 32.1561 | 2.2194 | 0.20017
2025-02-06 20:06 | 0.37797 | 0.42924 | 26.4527 | 0.042742 | 0.97864 | 0.41526 | 0.00089882 | 37086.3653 | 0.023649 | 1.6976 | 27.8133 | 32.4126 | 2.2443 | 0.2024
2025-02-06 20:07 | 0.37334 | 0.42398 | 26.4522 | 0.042788 | 0.97864 | 0.41017 | 0.00088781 | 36631.6821 | 0.023649 | 1.6976 | 27.5198 | 32.0703 | 2.2205 | 0.20026
2025-02-06 20:08 | 0.36678 | 0.41652 | 26.4515 | 0.042784 | 0.97864 | 0.40296 | 0.0008722 | 35987.5656 | 0.023649 | 1.6976 | 27.1032 | 31.5843 | 2.1831 | 0.19689
2025-02-06 20:09 | 0.3633 | 0.41258 | 26.4509 | 0.042748 | 0.97864 | 0.39914 | 0.00086393 | 35646.5067 | 0.02365 | 1.6975 | 26.8823 | 31.3264 | 2.1616 | 0.19495
2025-02-06 20:10 | 0.36987 | 0.42003 | 26.4503 | 0.042761 | 0.97864 | 0.40635 | 0.00087954 | 36290.3662 | 0.02365 | 1.6975 | 27.2994 | 31.812 | 2.1993 | 0.19835
2025-02-06 20:11 | 0.36948 | 0.41959 | 26.4496 | 0.042815 | 0.97864 | 0.40592 | 0.00087862 | 36252.3622 | 0.023651 | 1.6975 | 27.2749 | 31.7829 | 2.1999 | 0.1984
2025-02-06 20:12 | 0.36716 | 0.41696 | 26.4492 | 0.042735 | 0.97864 | 0.40338 | 0.00087312 | 36024.9837 | 0.023651 | 1.6975 | 27.1278 | 31.6111 | 2.1827 | 0.19685
2025-02-06 20:13 | 0.37334 | 0.42397 | 26.4487 | 0.042648 | 0.97865 | 0.41017 | 0.00088781 | 36630.9968 | 0.023651 | 1.6974 | 27.5198 | 32.0677 | 2.213 | 0.19958
2025-02-06 20:14 | 0.38608 | 0.43844 | 26.4483 | 0.04263 | 0.97865 | 0.42416 | 0.0009181 | 37880.9834 | 0.023652 | 1.6974 | 28.3256 | 33.0062 | 2.2837 | 0.20596
2025-02-06 20:15 | 0.39612 | 0.44984 | 26.4479 | 0.042708 | 0.97865 | 0.43519 | 0.00094197 | 38865.7983 | 0.023652 | 1.6974 | 28.9578 | 33.7426 | 2.3443 | 0.21142
2025-02-06 20:16 | 0.38956 | 0.44238 | 26.4474 | 0.042595 | 0.97865 | 0.42798 | 0.00092637 | 38221.7332 | 0.023652 | 1.6974 | 28.5447 | 33.2609 | 2.3013 | 0.20755
2025-02-06 20:17 | 0.40693 | 0.46211 | 26.447 | 0.042513 | 0.97865 | 0.44707 | 0.00096768 | 39926.2763 | 0.023653 | 1.6974 | 29.6361 | 34.5323 | 2.394 | 0.21591
2025-02-06 20:18 | 0.3911 | 0.44413 | 26.4466 | 0.042523 | 0.97865 | 0.42968 | 0.00093004 | 38373.0781 | 0.023653 | 1.6973 | 28.642 | 33.3736 | 2.3059 | 0.20797
2025-02-06 20:19 | 0.37102 | 0.42133 | 26.4462 | 0.042585 | 0.97865 | 0.40762 | 0.0008823 | 36403.2021 | 0.023653 | 1.6973 | 27.3729 | 31.8945 | 2.1966 | 0.1981
2025-02-06 20:20 | 0.38647 | 0.43887 | 26.4457 | 0.042549 | 0.97865 | 0.42459 | 0.00091902 | 37918.3345 | 0.023653 | 1.6973 | 28.3499 | 33.0326 | 2.2813 | 0.20575
2025-02-06 20:21 | 0.38145 | 0.43317 | 26.4453 | 0.042553 | 0.97865 | 0.41907 | 0.00090709 | 37425.7924 | 0.023654 | 1.6973 | 28.033 | 32.663 | 2.2534 | 0.20322
2025-02-06 20:22 | 0.36678 | 0.41651 | 26.4444 | 0.04261 | 0.97865 | 0.40296 | 0.0008722 | 35986.1764 | 0.023654 | 1.6972 | 27.1032 | 31.579 | 2.1738 | 0.19605
2025-02-06 20:23 | 0.35751 | 0.40598 | 26.4435 | 0.042196 | 0.97866 | 0.39278 | 0.00085016 | 35076.8767 | 0.023655 | 1.6972 | 26.5133 | 30.891 | 2.1009 | 0.18948
2025-02-06 20:24 | 0.35404 | 0.40203 | 26.4426 | 0.042302 | 0.97866 | 0.38896 | 0.0008419 | 34735.7822 | 0.023656 | 1.6972 | 26.2916 | 30.6319 | 2.0867 | 0.18819
2025-02-06 20:25 | 0.37411 | 0.42483 | 26.4417 | 0.042471 | 0.97866 | 0.41101 | 0.00088964 | 36705.3496 | 0.023656 | 1.6971 | 27.5688 | 32.1193 | 2.2077 | 0.1991
2025-02-06 20:26 | 0.39071 | 0.44368 | 26.4407 | 0.042426 | 0.97866 | 0.42925 | 0.00092912 | 38333.982 | 0.023657 | 1.6971 | 28.6177 | 33.3406 | 2.2982 | 0.20727
2025-02-06 20:27 | 0.38183 | 0.43359 | 26.4398 | 0.042428 | 0.97866 | 0.4195 | 0.000908 | 37462.5672 | 0.023658 | 1.697 | 28.0574 | 32.6872 | 2.2485 | 0.20279
2025-02-06 20:28 | 0.38454 | 0.43666 | 26.4389 | 0.042353 | 0.97867 | 0.42247 | 0.00091443 | 37727.5436 | 0.023658 | 1.697 | 28.2281 | 32.8854 | 2.2596 | 0.20379
2025-02-06 20:29 | 0.38454 | 0.43666 | 26.4384 | 0.04243 | 0.97867 | 0.42247 | 0.00091443 | 37727.4399 | 0.023659 | 1.697 | 28.2281 | 32.885 | 2.2637 | 0.20416
2025-02-06 20:30 | 0.37875 | 0.43008 | 26.438 | 0.042388 | 0.97867 | 0.4161 | 0.00090066 | 37159.1688 | 0.023659 | 1.697 | 27.8621 | 32.4583 | 2.229 | 0.20103
2025-02-06 20:31 | 0.37064 | 0.42088 | 26.4376 | 0.042433 | 0.97867 | 0.4072 | 0.00088138 | 36363.6275 | 0.023659 | 1.6969 | 27.3484 | 31.8595 | 2.186 | 0.19715
2025-02-06 20:32 | 0.38608 | 0.43841 | 26.4371 | 0.042334 | 0.97867 | 0.42416 | 0.0009181 | 37878.6909 | 0.023659 | 1.6969 | 28.3256 | 32.9975 | 2.2671 | 0.20446
2025-02-06 20:33 | 0.38647 | 0.43885 | 26.4367 | 0.042204 | 0.97867 | 0.42459 | 0.00091902 | 37916.4812 | 0.02366 | 1.6969 | 28.3499 | 33.0255 | 2.2622 | 0.20403
2025-02-06 20:34 | 0.3606 | 0.40947 | 26.4363 | 0.042225 | 0.97867 | 0.39617 | 0.00085751 | 35378.532 | 0.02366 | 1.6969 | 26.7102 | 31.115 | 2.1192 | 0.19112
2025-02-06 20:35 | 0.36407 | 0.41342 | 26.4359 | 0.042118 | 0.97867 | 0.39999 | 0.00086577 | 35719.3565 | 0.02366 | 1.6969 | 26.9314 | 31.3724 | 2.1331 | 0.19238
2025-02-06 20:36 | 0.35944 | 0.40816 | 26.4354 | 0.042237 | 0.97867 | 0.3949 | 0.00085475 | 35264.7329 | 0.023661 | 1.6968 | 26.6364 | 31.0284 | 2.1132 | 0.19059
2025-02-06 20:37 | 0.36253 | 0.41166 | 26.435 | 0.042353 | 0.97867 | 0.39829 | 0.0008621 | 35567.6763 | 0.023661 | 1.6968 | 26.8331 | 31.2573 | 2.1363 | 0.19267
2025-02-06 20:38 | 0.36678 | 0.41648 | 26.4346 | 0.042354 | 0.97867 | 0.40296 | 0.0008722 | 35984.2564 | 0.023661 | 1.6968 | 27.1032 | 31.5716 | 2.1601 | 0.19482
2025-02-06 20:39 | 0.3633 | 0.41254 | 26.4343 | 0.042346 | 0.97867 | 0.39914 | 0.00086393 | 35643.2901 | 0.023662 | 1.6968 | 26.8823 | 31.314 | 2.1403 | 0.19302
2025-02-06 20:40 | 0.36987 | 0.41999 | 26.4339 | 0.042391 | 0.97868 | 0.40635 | 0.00087954 | 36287.1576 | 0.023662 | 1.6968 | 27.2994 | 31.7997 | 2.1793 | 0.19654
2025-02-06 20:41 | 0.37334 | 0.42394 | 26.4336 | 0.042182 | 0.97868 | 0.41017 | 0.00088781 | 36627.999 | 0.023662 | 1.6968 | 27.5198 | 32.0562 | 2.1878 | 0.19732
2025-02-06 20:42 | 0.37643 | 0.42744 | 26.4333 | 0.042118 | 0.97868 | 0.41356 | 0.00089515 | 36930.9606 | 0.023662 | 1.6967 | 27.7155 | 32.2839 | 2.2017 | 0.19857
2025-02-06 20:43 | 0.38647 | 0.43884 | 26.433 | 0.042118 | 0.97868 | 0.42459 | 0.00091902 | 37915.7225 | 0.023662 | 1.6967 | 28.3499 | 33.0226 | 2.2574 | 0.20359
2025-02-06 20:44 | 0.40654 | 0.46164 | 26.4327 | 0.042217 | 0.97868 | 0.44664 | 0.00096676 | 39885.3036 | 0.023663 | 1.6967 | 29.612 | 34.4924 | 2.3741 | 0.21412
2025-02-06 20:45 | 0.41928 | 0.4761 | 26.4324 | 0.042089 | 0.97868 | 0.46064 | 0.00099706 | 41135.1952 | 0.023663 | 1.6967 | 30.4083 | 35.4198 | 2.4373 | 0.21982
2025-02-06 20:46 | 0.39149 | 0.44454 | 26.4318 | 0.042077 | 0.97868 | 0.4301 | 0.00093096 | 38407.8765 | 0.023663 | 1.6967 | 28.6663 | 33.3902 | 2.2829 | 0.20589
2025-02-06 20:47 | 0.39264 | 0.44585 | 26.4311 | 0.042077 | 0.97868 | 0.43137 | 0.00093371 | 38521.3756 | 0.023664 | 1.6967 | 28.7392 | 33.4746 | 2.2893 | 0.20646
2025-02-06 20:48 | 0.4189 | 0.47566 | 26.4305 | 0.042115 | 0.97868 | 0.46022 | 0.00099614 | 41096.899 | 0.023664 | 1.6966 | 30.3842 | 35.3901 | 2.4365 | 0.21974
2025-02-06 20:49 | 0.42353 | 0.48092 | 26.4298 | 0.042217 | 0.97868 | 0.46531 | 0.0010072 | 41551.2819 | 0.023665 | 1.6966 | 30.673 | 35.7259 | 2.468 | 0.22258
2025-02-06 20:50 | 0.42044 | 0.47741 | 26.4293 | 0.042051 | 0.97868 | 0.46191 | 0.00099981 | 41248.1377 | 0.023665 | 1.6966 | 30.4805 | 35.5013 | 2.4413 | 0.22017
2025-02-06 20:51 | 0.41426 | 0.47039 | 26.4294 | 0.041918 | 0.97868 | 0.45513 | 0.00098512 | 40642.1236 | 0.023665 | 1.6966 | 30.095 | 35.0523 | 2.3996 | 0.21641
2025-02-06 20:52 | 0.42276 | 0.48004 | 26.4296 | 0.041994 | 0.97868 | 0.46446 | 0.0010053 | 41475.4693 | 0.023665 | 1.6966 | 30.6249 | 35.6697 | 2.4507 | 0.22102
2025-02-06 20:53 | 0.41542 | 0.47171 | 26.4298 | 0.042061 | 0.97868 | 0.4564 | 0.00098788 | 40755.8512 | 0.023665 | 1.6966 | 30.1674 | 35.1369 | 2.4142 | 0.21773
2025-02-06 20:54 | 0.41504 | 0.47127 | 26.43 | 0.042032 | 0.97868 | 0.45598 | 0.00098696 | 40718.0217 | 0.023665 | 1.6966 | 30.1432 | 35.109 | 2.4104 | 0.21739
2025-02-06 20:55 | 0.42546 | 0.48311 | 26.4301 | 0.04202 | 0.97868 | 0.46743 | 0.0010117 | 41740.737 | 0.023664 | 1.6966 | 30.7932 | 35.8662 | 2.4671 | 0.2225
2025-02-06 20:56 | 0.37913 | 0.4305 | 26.4296 | 0.041966 | 0.97868 | 0.41653 | 0.00090158 | 37195.3612 | 0.023665 | 1.6966 | 27.8865 | 32.4803 | 2.2084 | 0.19917
2025-02-06 20:57 | 0.36562 | 0.41516 | 26.429 | 0.041921 | 0.97869 | 0.40168 | 0.00086944 | 35869.5347 | 0.023665 | 1.6966 | 27.0296 | 31.4817 | 2.1313 | 0.19222
2025-02-06 20:58 | 0.38068 | 0.43225 | 26.4283 | 0.042 | 0.97869 | 0.41823 | 0.00090525 | 37346.6087 | 0.023666 | 1.6965 | 27.9842 | 32.593 | 2.2187 | 0.2001
2025-02-06 20:59 | 0.38106 | 0.43269 | 26.4277 | 0.04194 | 0.97869 | 0.41865 | 0.00090617 | 37384.3538 | 0.023666 | 1.6965 | 28.0086 | 32.6209 | 2.2176 | 0.2
2025-02-06 21:00 | 0.37759 | 0.42874 | 26.4271 | 0.041934 | 0.97869 | 0.41483 | 0.0008979 | 37043.3418 | 0.023667 | 1.6965 | 27.7888 | 32.3645 | 2.1981 | 0.19824
2025-02-06 21:01 | 0.3633 | 0.41252 | 26.4268 | 0.041944 | 0.97869 | 0.39914 | 0.00086393 | 35641.8546 | 0.023667 | 1.6965 | 26.8823 | 31.3085 | 2.1195 | 0.19115
2025-02-06 21:02 | 0.39303 | 0.44628 | 26.4266 | 0.041999 | 0.97869 | 0.4318 | 0.00093463 | 38558.3058 | 0.023667 | 1.6964 | 28.7635 | 33.4993 | 2.2869 | 0.20625
2025-02-06 21:03 | 0.42121 | 0.47828 | 26.4264 | 0.042081 | 0.97869 | 0.46276 | 0.0010016 | 41323.2446 | 0.023667 | 1.6964 | 30.5287 | 35.5549 | 2.4471 | 0.22069
2025-02-06 21:04 | 0.39226 | 0.4454 | 26.4262 | 0.042031 | 0.97869 | 0.43095 | 0.00093279 | 38482.4632 | 0.023667 | 1.6964 | 28.7149 | 33.4423 | 2.2843 | 0.20602
2025-02-06 21:05 | 0.38222 | 0.434 | 26.426 | 0.041752 | 0.97869 | 0.41992 | 0.00090892 | 37497.6466 | 0.023667 | 1.6964 | 28.0818 | 32.7049 | 2.214 | 0.19967
2025-02-06 21:06 | 0.39264 | 0.44584 | 26.4264 | 0.04188 | 0.97869 | 0.43137 | 0.00093371 | 38520.3809 | 0.023667 | 1.6964 | 28.7392 | 33.4708 | 2.2783 | 0.20547
2025-02-06 21:07 | 0.38454 | 0.43663 | 26.4268 | 0.042092 | 0.97869 | 0.42247 | 0.00091443 | 37725.062 | 0.023667 | 1.6965 | 28.2281 | 32.8759 | 2.2449 | 0.20246
2025-02-06 21:08 | 0.37488 | 0.42567 | 26.4272 | 0.04209 | 0.97869 | 0.41186 | 0.00089148 | 36778.2334 | 0.023666 | 1.6965 | 27.6177 | 32.1653 | 2.1913 | 0.19763
2025-02-06 21:09 | 0.35944 | 0.40814 | 26.4277 | 0.041662 | 0.97869 | 0.3949 | 0.00085475 | 35263.2484 | 0.023666 | 1.6965 | 26.6364 | 31.0227 | 2.084 | 0.18795
2025-02-06 21:10 | 0.35674 | 0.40507 | 26.4279 | 0.041578 | 0.97869 | 0.39193 | 0.00084833 | 34998.1519 | 0.023666 | 1.6965 | 26.4641 | 30.8222 | 2.065 | 0.18623
2025-02-06 21:11 | 0.35674 | 0.40507 | 26.4266 | 0.041692 | 0.97869 | 0.39193 | 0.00084833 | 34997.9189 | 0.023667 | 1.6964 | 26.4641 | 30.8213 | 2.0706 | 0.18674
2025-02-06 21:12 | 0.35481 | 0.40287 | 26.4251 | 0.041871 | 0.97869 | 0.38981 | 0.00084374 | 34808.2531 | 0.023668 | 1.6964 | 26.3409 | 30.6767 | 2.0687 | 0.18657
2025-02-06 21:13 | 0.35211 | 0.3998 | 26.4236 | 0.041866 | 0.9787 | 0.38684 | 0.00083731 | 34542.8385 | 0.023669 | 1.6963 | 26.1682 | 30.4746 | 2.0533 | 0.18518
2025-02-06 21:14 | 0.35983 | 0.40857 | 26.4221 | 0.041837 | 0.9787 | 0.39532 | 0.00085567 | 35300.0698 | 0.02367 | 1.6962 | 26.661 | 31.0473 | 2.0946 | 0.1889
2025-02-06 21:15 | 0.36485 | 0.41426 | 26.4206 | 0.041929 | 0.9787 | 0.40083 | 0.00086761 | 35792.1567 | 0.023671 | 1.6962 | 26.9805 | 31.4183 | 2.1269 | 0.19182
2025-02-06 21:16 | 0.37218 | 0.42259 | 26.4189 | 0.041748 | 0.97871 | 0.40889 | 0.00088505 | 36511.4526 | 0.023672 | 1.6961 | 27.4464 | 31.9595 | 2.1581 | 0.19463
2025-02-06 21:17 | 0.38222 | 0.43398 | 26.4172 | 0.041597 | 0.97871 | 0.41992 | 0.00090892 | 37495.8521 | 0.023674 | 1.696 | 28.0818 | 32.6981 | 2.2052 | 0.19888
2025-02-06 21:18 | 0.37566 | 0.42652 | 26.4155 | 0.041687 | 0.97871 | 0.41271 | 0.00089331 | 36851.6394 | 0.023675 | 1.6959 | 27.6666 | 32.2133 | 2.1738 | 0.19605
2025-02-06 21:19 | 0.3911 | 0.44405 | 26.4138 | 0.041685 | 0.97872 | 0.42968 | 0.00093004 | 38366.2507 | 0.023676 | 1.6959 | 28.642 | 33.3476 | 2.2583 | 0.20367
2025-02-06 21:20 | 0.40925 | 0.46465 | 26.4123 | 0.041682 | 0.97872 | 0.44961 | 0.00097319 | 40145.9974 | 0.023677 | 1.6958 | 29.7812 | 34.6727 | 2.3575 | 0.21261
2025-02-06 21:21 | 0.41349 | 0.46947 | 26.4121 | 0.041762 | 0.97872 | 0.45428 | 0.00098329 | 40562.5814 | 0.023677 | 1.6958 | 30.0468 | 34.9818 | 2.3852 | 0.21512
2025-02-06 21:22 | 0.38338 | 0.43528 | 26.4123 | 0.041679 | 0.97872 | 0.42119 | 0.00091168 | 37608.471 | 0.023677 | 1.6958 | 28.155 | 32.7794 | 2.2156 | 0.19982
2025-02-06 21:23 | 0.39651 | 0.45019 | 26.4124 | 0.041648 | 0.97872 | 0.43562 | 0.00094289 | 38896.2022 | 0.023677 | 1.6958 | 28.9821 | 33.7425 | 2.2858 | 0.20616
2025-02-06 21:24 | 0.40307 | 0.45764 | 26.4125 | 0.041759 | 0.97872 | 0.44283 | 0.0009585 | 39540.0812 | 0.023677 | 1.6958 | 29.3942 | 34.2224 | 2.328 | 0.20995
2025-02-06 21:25 | 0.36485 | 0.41424 | 26.4127 | 0.041669 | 0.97872 | 0.40083 | 0.00086761 | 35790.6169 | 0.023677 | 1.6958 | 26.9805 | 31.4123 | 2.1132 | 0.19059
2025-02-06 21:26 | 0.36253 | 0.41161 | 26.4128 | 0.041581 | 0.97872 | 0.39829 | 0.0008621 | 35563.4006 | 0.023677 | 1.6958 | 26.8331 | 31.2408 | 2.0961 | 0.18904
2025-02-06 21:27 | 0.37257 | 0.42301 | 26.4129 | 0.041664 | 0.97872 | 0.40932 | 0.00088597 | 36548.1445 | 0.023677 | 1.6958 | 27.4709 | 31.9834 | 2.1554 | 0.19439
2025-02-06 21:28 | 0.37141 | 0.4217 | 26.413 | 0.041695 | 0.97872 | 0.40805 | 0.00088321 | 36434.5323 | 0.023677 | 1.6958 | 27.3974 | 31.898 | 2.1507 | 0.19397
2025-02-06 21:29 | 0.366 | 0.41556 | 26.4124 | 0.041573 | 0.97872 | 0.40211 | 0.00087036 | 35904.1939 | 0.023677 | 1.6958 | 27.0542 | 31.4979 | 2.1147 | 0.19072
2025-02-06 21:30 | 0.36214 | 0.41117 | 26.4118 | 0.04164 | 0.97872 | 0.39787 | 0.00086118 | 35525.3328 | 0.023677 | 1.6958 | 26.8085 | 31.2115 | 2.0968 | 0.18911
2025-02-06 21:31 | 0.35674 | 0.40503 | 26.4112 | 0.04178 | 0.97872 | 0.39193 | 0.00084833 | 34994.9807 | 0.023678 | 1.6958 | 26.4641 | 30.81 | 2.074 | 0.18705
2025-02-06 21:32 | 0.34323 | 0.38969 | 26.4105 | 0.041737 | 0.97872 | 0.37708 | 0.00081619 | 33669.2957 | 0.023678 | 1.6957 | 25.5997 | 29.8032 | 1.9971 | 0.18012
2025-02-06 21:33 | 0.3301 | 0.37479 | 26.4099 | 0.04152 | 0.97872 | 0.36266 | 0.00078498 | 32381.4984 | 0.023679 | 1.6957 | 24.7554 | 28.8198 | 1.9144 | 0.17265
2025-02-06 21:34 | 0.34979 | 0.39714 | 26.4094 | 0.04136 | 0.97873 | 0.38429 | 0.0008318 | 34312.9419 | 0.023679 | 1.6957 | 26.0201 | 30.2919 | 2.015 | 0.18173
2025-02-06 21:35 | 0.39496 | 0.44843 | 26.409 | 0.041327 | 0.97873 | 0.43392 | 0.00093922 | 38743.9921 | 0.023679 | 1.6957 | 28.885 | 33.6267 | 2.2597 | 0.20379
2025-02-06 21:36 | 0.46059 | 0.52294 | 26.4086 | 0.041404 | 0.97873 | 0.50603 | 0.0010953 | 45182.2817 | 0.02368 | 1.6956 | 32.9678 | 38.3793 | 2.6194 | 0.23624
2025-02-06 21:37 | 0.50345 | 0.5716 | 26.4081 | 0.041554 | 0.97873 | 0.55311 | 0.0011972 | 49386.0524 | 0.02368 | 1.6956 | 35.5891 | 41.4306 | 2.8602 | 0.25795
2025-02-06 21:38 | 0.51233 | 0.58168 | 26.4077 | 0.041609 | 0.97873 | 0.56286 | 0.0012183 | 50257.0083 | 0.02368 | 1.6956 | 36.1283 | 42.0578 | 2.9118 | 0.26261
2025-02-06 21:39 | 0.5077 | 0.57642 | 26.4073 | 0.041701 | 0.97873 | 0.55777 | 0.0012073 | 49802.4118 | 0.023681 | 1.6956 | 35.8472 | 41.7301 | 2.8932 | 0.26093
2025-02-06 21:40 | 0.52623 | 0.59746 | 26.4068 | 0.041919 | 0.97873 | 0.57813 | 0.0012514 | 51620.1657 | 0.023681 | 1.6956 | 36.9696 | 43.0363 | 3.0087 | 0.27135
2025-02-06 21:41 | 0.54244 | 0.61586 | 26.4063 | 0.042078 | 0.97873 | 0.59595 | 0.0012899 | 53210.678 | 0.023681 | 1.6955 | 37.9473 | 44.1739 | 3.1082 | 0.28032
2025-02-06 21:42 | 0.52353 | 0.59438 | 26.4059 | 0.042133 | 0.97873 | 0.57517 | 0.0012449 | 51354.8046 | 0.023682 | 1.6955 | 36.8063 | 42.8452 | 3.0093 | 0.2714
2025-02-06 21:43 | 0.52932 | 0.60096 | 26.4054 | 0.042192 | 0.97873 | 0.58153 | 0.0012587 | 51922.7598 | 0.023682 | 1.6955 | 37.1562 | 43.252 | 3.0451 | 0.27463
2025-02-06 21:44 | 0.53742 | 0.61016 | 26.405 | 0.042296 | 0.97873 | 0.59044 | 0.001278 | 52717.9448 | 0.023682 | 1.6955 | 37.6451 | 43.8207 | 3.0968 | 0.27929
2025-02-06 21:45 | 0.53549 | 0.60797 | 26.4045 | 0.042426 | 0.97874 | 0.58831 | 0.0012734 | 52528.4419 | 0.023683 | 1.6955 | 37.5288 | 43.6848 | 3.0957 | 0.27919
2025-02-06 21:46 | 0.53858 | 0.61147 | 26.4037 | 0.042512 | 0.97874 | 0.59171 | 0.0012808 | 52831.2083 | 0.023683 | 1.6954 | 37.7149 | 43.9006 | 3.1189 | 0.28128
2025-02-06 21:47 | 0.5409 | 0.6141 | 26.403 | 0.042562 | 0.97874 | 0.59425 | 0.0012863 | 53058.2186 | 0.023684 | 1.6954 | 37.8543 | 44.0622 | 3.1352 | 0.28276
2025-02-06 21:48 | 0.54051 | 0.61366 | 26.4022 | 0.04261 | 0.97874 | 0.59383 | 0.0012853 | 53020.125 | 0.023684 | 1.6954 | 37.8311 | 44.0343 | 3.1365 | 0.28288
2025-02-06 21:49 | 0.5436 | 0.61716 | 26.4014 | 0.042658 | 0.97874 | 0.59722 | 0.0012927 | 53322.875 | 0.023685 | 1.6953 | 38.0169 | 44.2498 | 3.157 | 0.28472
2025-02-06 21:50 | 0.54051 | 0.61365 | 26.4007 | 0.042705 | 0.97874 | 0.59383 | 0.0012853 | 53019.6838 | 0.023685 | 1.6953 | 37.8311 | 44.0327 | 3.1434 | 0.2835
2025-02-06 21:51 | 0.55518 | 0.63031 | 26.3999 | 0.04282 | 0.97874 | 0.60995 | 0.0013202 | 54458.5633 | 0.023686 | 1.6952 | 38.7125 | 45.0578 | 3.2327 | 0.29155
2025-02-06 21:52 | 0.56445 | 0.64082 | 26.3992 | 0.043073 | 0.97875 | 0.62013 | 0.0013423 | 55367.2765 | 0.023686 | 1.6952 | 39.2675 | 45.7031 | 3.3031 | 0.2979
2025-02-06 21:53 | 0.57951 | 0.65792 | 26.3993 | 0.043146 | 0.97875 | 0.63667 | 0.0013781 | 56844.2557 | 0.023686 | 1.6952 | 40.1667 | 46.7497 | 3.3922 | 0.30593
2025-02-06 21:54 | 0.58337 | 0.6623 | 26.3994 | 0.043228 | 0.97875 | 0.64091 | 0.0013873 | 57223.0125 | 0.023686 | 1.6952 | 40.3967 | 47.0176 | 3.4201 | 0.30845
2025-02-06 21:55 | 0.55634 | 0.63162 | 26.3996 | 0.04329 | 0.97875 | 0.61122 | 0.001323 | 54572.0914 | 0.023686 | 1.6952 | 38.782 | 45.1383 | 3.2746 | 0.29533
2025-02-06 21:56 | 0.54129 | 0.61453 | 26.3997 | 0.043383 | 0.97875 | 0.59468 | 0.0012872 | 53095.1672 | 0.023686 | 1.6952 | 37.8776 | 44.0858 | 3.1975 | 0.28838
2025-02-06 21:57 | 0.54862 | 0.62286 | 26.3999 | 0.043549 | 0.97874 | 0.60274 | 0.0013046 | 53814.7597 | 0.023686 | 1.6952 | 38.3186 | 44.5993 | 3.2509 | 0.29319
2025-02-06 21:58 | 0.55711 | 0.6325 | 26.4001 | 0.043812 | 0.97874 | 0.61207 | 0.0013248 | 54647.967 | 0.023686 | 1.6953 | 38.8282 | 45.1927 | 3.3186 | 0.29929
2025-02-06 21:59 | 0.55171 | 0.62636 | 26.4002 | 0.043796 | 0.97874 | 0.60613 | 0.001312 | 54117.8117 | 0.023686 | 1.6953 | 38.5041 | 44.8155 | 3.2868 | 0.29643
2025-02-06 22:00 | 0.55789 | 0.63338 | 26.4002 | 0.04391 | 0.97874 | 0.61292 | 0.0013267 | 54723.7556 | 0.023686 | 1.6953 | 38.8745 | 45.2467 | 3.3303 | 0.30035
2025-02-06 22:01 | 0.58337 | 0.66231 | 26.4002 | 0.044272 | 0.97874 | 0.64091 | 0.0013873 | 57223.2494 | 0.023686 | 1.6953 | 40.3967 | 47.0184 | 3.5028 | 0.31591
2025-02-06 22:02 | 0.54862 | 0.62286 | 26.4002 | 0.044396 | 0.97874 | 0.60274 | 0.0013046 | 53814.8487 | 0.023686 | 1.6953 | 38.3186 | 44.5997 | 3.3142 | 0.2989
2025-02-06 22:03 | 0.54013 | 0.61321 | 26.4002 | 0.044572 | 0.97874 | 0.5934 | 0.0012844 | 52981.684 | 0.023686 | 1.6953 | 37.8078 | 44.0052 | 3.2786 | 0.29568
2025-02-06 22:04 | 0.55634 | 0.63162 | 26.4002 | 0.04484 | 0.97874 | 0.61122 | 0.001323 | 54572.272 | 0.023686 | 1.6953 | 38.782 | 45.139 | 3.392 | 0.30591
2025-02-06 22:05 | 0.55673 | 0.63206 | 26.4002 | 0.045058 | 0.97874 | 0.61164 | 0.0013239 | 54610.1436 | 0.023686 | 1.6953 | 38.8051 | 45.1659 | 3.4106 | 0.3076
2025-02-06 22:06 | 0.57024 | 0.6474 | 26.4003 | 0.045286 | 0.97874 | 0.62649 | 0.001356 | 55935.6572 | 0.023685 | 1.6953 | 39.6138 | 46.1072 | 3.5067 | 0.31626
2025-02-06 22:07 | 0.55905 | 0.63469 | 26.4009 | 0.045667 | 0.97874 | 0.61419 | 0.0013294 | 54837.5629 | 0.023685 | 1.6953 | 38.9439 | 45.3282 | 3.4704 | 0.31299
2025-02-06 22:08 | 0.56986 | 0.64697 | 26.4015 | 0.04586 | 0.97874 | 0.62607 | 0.0013551 | 55898.1548 | 0.023685 | 1.6953 | 39.5907 | 46.0817 | 3.5489 | 0.32007
2025-02-06 22:09 | 0.57565 | 0.65355 | 26.4022 | 0.046128 | 0.97874 | 0.63243 | 0.0013689 | 56466.4233 | 0.023684 | 1.6954 | 39.9365 | 46.4848 | 3.6041 | 0.32504
2025-02-06 22:10 | 0.57796 | 0.65618 | 26.4028 | 0.046392 | 0.97874 | 0.63497 | 0.0013744 | 56693.8508 | 0.023684 | 1.6954 | 40.0746 | 46.6464 | 3.6386 | 0.32815
2025-02-06 22:11 | 0.56213 | 0.63821 | 26.4033 | 0.046651 | 0.97874 | 0.61758 | 0.0013368 | 55141.2501 | 0.023683 | 1.6954 | 39.1289 | 45.5461 | 3.564 | 0.32143
2025-02-06 22:12 | 0.55711 | 0.63251 | 26.4028 | 0.046793 | 0.97874 | 0.61207 | 0.0013248 | 54648.7672 | 0.023684 | 1.6954 | 38.8282 | 45.1956 | 3.5446 | 0.31968
2025-02-06 22:13 | 0.5575 | 0.63295 | 26.4021 | 0.047102 | 0.97874 | 0.61249 | 0.0013257 | 54686.4495 | 0.023684 | 1.6953 | 38.8514 | 45.2218 | 3.5703 | 0.322
2025-02-06 22:14 | 0.55441 | 0.62944 | 26.4015 | 0.047233 | 0.97874 | 0.6091 | 0.0013184 | 54383.2882 | 0.023685 | 1.6953 | 38.6662 | 45.0056 | 3.5614 | 0.32119
2025-02-06 22:15 | 0.56715 | 0.6439 | 26.4008 | 0.04737 | 0.97874 | 0.6231 | 0.0013487 | 55632.8492 | 0.023685 | 1.6953 | 39.4292 | 45.8929 | 3.6493 | 0.32912
2025-02-06 22:16 | 0.56986 | 0.64697 | 26.4003 | 0.047714 | 0.97874 | 0.62607 | 0.0013551 | 55897.8014 | 0.023685 | 1.6953 | 39.5907 | 46.0804 | 3.6923 | 0.333
2025-02-06 22:17 | 0.56793 | 0.64477 | 26.4007 | 0.048004 | 0.97874 | 0.62394 | 0.0013505 | 55708.5476 | 0.023685 | 1.6953 | 39.4753 | 45.9465 | 3.7029 | 0.33395
2025-02-06 22:18 | 0.57874 | 0.65705 | 26.4011 | 0.048351 | 0.97874 | 0.63582 | 0.0013762 | 56769.0814 | 0.023685 | 1.6953 | 40.1207 | 46.6981 | 3.7969 | 0.34243
2025-02-06 22:19 | 0.59186 | 0.67195 | 26.4016 | 0.048769 | 0.97874 | 0.65024 | 0.0014075 | 58056.8512 | 0.023685 | 1.6953 | 40.902 | 47.6081 | 3.9119 | 0.3528
2025-02-06 22:20 | 0.57024 | 0.64741 | 26.4021 | 0.049036 | 0.97874 | 0.62649 | 0.001356 | 55936.1928 | 0.023684 | 1.6953 | 39.6138 | 46.1091 | 3.7973 | 0.34247
2025-02-06 22:21 | 0.56098 | 0.63689 | 26.4025 | 0.049482 | 0.97874 | 0.61631 | 0.001334 | 55027.412 | 0.023684 | 1.6954 | 39.0595 | 45.4645 | 3.7729 | 0.34026
2025-02-06 22:22 | 0.57256 | 0.65004 | 26.403 | 0.049715 | 0.97874 | 0.62903 | 0.0013615 | 56163.7005 | 0.023684 | 1.6954 | 39.7521 | 46.2712 | 3.8647 | 0.34855
2025-02-06 22:23 | 0.56793 | 0.64478 | 26.4034 | 0.050157 | 0.97874 | 0.62394 | 0.0013505 | 55709.3602 | 0.023683 | 1.6954 | 39.4753 | 45.9494 | 3.8693 | 0.34896
2025-02-06 22:24 | 0.56522 | 0.64172 | 26.4034 | 0.05063 | 0.97874 | 0.62098 | 0.0013441 | 55444.2718 | 0.023683 | 1.6954 | 39.3137 | 45.7614 | 3.8881 | 0.35066
2025-02-06 22:25 | 0.57294 | 0.65048 | 26.4034 | 0.050983 | 0.97874 | 0.62946 | 0.0013625 | 56201.7083 | 0.023683 | 1.6954 | 39.7752 | 46.2985 | 3.9659 | 0.35767
2025-02-06 22:26 | 0.57796 | 0.65618 | 26.4034 | 0.051326 | 0.97874 | 0.63497 | 0.0013744 | 56694.0425 | 0.023683 | 1.6954 | 40.0746 | 46.6471 | 4.0256 | 0.36306
2025-02-06 22:27 | 0.56986 | 0.64698 | 26.4034 | 0.051667 | 0.97874 | 0.62607 | 0.0013551 | 55898.7348 | 0.023683 | 1.6954 | 39.5907 | 46.0838 | 3.9986 | 0.36062
2025-02-06 22:28 | 0.5602 | 0.63602 | 26.4034 | 0.052236 | 0.97874 | 0.61546 | 0.0013322 | 54951.9405 | 0.023683 | 1.6954 | 39.0133 | 45.4117 | 3.9777 | 0.35874
2025-02-06 22:29 | 0.53318 | 0.60533 | 26.4034 | 0.05267 | 0.97874 | 0.58577 | 0.0012679 | 52300.9169 | 0.023683 | 1.6954 | 37.3891 | 43.5211 | 3.8273 | 0.34517
2025-02-06 22:30 | 0.52777 | 0.5992 | 26.4034 | 0.053 | 0.97874 | 0.57983 | 0.001255 | 51770.7187 | 0.023683 | 1.6954 | 37.0629 | 43.1415 | 3.8143 | 0.344
2025-02-06 22:31 | 0.5602 | 0.63602 | 26.4036 | 0.053388 | 0.97874 | 0.61546 | 0.0013322 | 54951.9881 | 0.023683 | 1.6954 | 39.0133 | 45.4119 | 4.0655 | 0.36666
2025-02-06 22:32 | 0.57333 | 0.65092 | 26.4037 | 0.053696 | 0.97874 | 0.62988 | 0.0013634 | 56239.6753 | 0.023683 | 1.6954 | 39.7982 | 46.3257 | 4.1796 | 0.37695
2025-02-06 22:33 | 0.56715 | 0.64391 | 26.4039 | 0.054015 | 0.97874 | 0.6231 | 0.0013487 | 55633.7724 | 0.023683 | 1.6954 | 39.4292 | 45.8963 | 4.1616 | 0.37532
2025-02-06 22:34 | 0.57565 | 0.65355 | 26.404 | 0.054328 | 0.97874 | 0.63243 | 0.0013689 | 56467.0017 | 0.023683 | 1.6954 | 39.9365 | 46.4869 | 4.245 | 0.38285
2025-02-06 22:35 | 0.56638 | 0.64303 | 26.4042 | 0.054605 | 0.97874 | 0.62225 | 0.0013469 | 55558.1218 | 0.023683 | 1.6954 | 39.383 | 45.8428 | 4.2016 | 0.37894
2025-02-06 22:36 | 0.56136 | 0.63734 | 26.4044 | 0.054732 | 0.97874 | 0.61673 | 0.0013349 | 55065.8309 | 0.023683 | 1.6954 | 39.0827 | 45.4934 | 4.1761 | 0.37663
2025-02-06 22:37 | 0.5826 | 0.66144 | 26.4045 | 0.055071 | 0.97874 | 0.64006 | 0.0013854 | 57148.843 | 0.023682 | 1.6955 | 40.3507 | 46.9697 | 4.3523 | 0.39252
2025-02-06 22:38 | 0.57449 | 0.65224 | 26.4048 | 0.055287 | 0.97873 | 0.63116 | 0.0013661 | 56353.6195 | 0.023682 | 1.6955 | 39.8673 | 46.4073 | 4.3118 | 0.38887
2025-02-06 22:39 | 0.57835 | 0.65663 | 26.4051 | 0.055597 | 0.97873 | 0.6354 | 0.0013753 | 56732.4357 | 0.023682 | 1.6955 | 40.0976 | 46.6758 | 4.3636 | 0.39354
2025-02-06 22:40 | 0.57989 | 0.65838 | 26.4054 | 0.055748 | 0.97873 | 0.63709 | 0.001379 | 56884.0192 | 0.023682 | 1.6955 | 40.1897 | 46.7833 | 4.3865 | 0.39561
2025-02-06 22:41 | 0.57256 | 0.65005 | 26.4057 | 0.055827 | 0.97873 | 0.62903 | 0.0013615 | 56164.54 | 0.023682 | 1.6955 | 39.7521 | 46.2742 | 4.3402 | 0.39143
2025-02-06 22:42 | 0.56793 | 0.64479 | 26.406 | 0.055829 | 0.97873 | 0.62394 | 0.0013505 | 55710.1664 | 0.023681 | 1.6955 | 39.4753 | 45.9523 | 4.3071 | 0.38845
2025-02-06 22:43 | 0.55364 | 0.62858 | 26.4064 | 0.055929 | 0.97873 | 0.60825 | 0.0013166 | 54308.9812 | 0.023681 | 1.6955 | 38.6199 | 44.9569 | 4.2121 | 0.37988
2025-02-06 22:44 | 0.54901 | 0.62332 | 26.4066 | 0.055732 | 0.97873 | 0.60316 | 0.0013055 | 53854.5892 | 0.023681 | 1.6956 | 38.3418 | 44.6334 | 4.164 | 0.37554
2025-02-06 22:45 | 0.57487 | 0.65269 | 26.4066 | 0.055535 | 0.97873 | 0.63158 | 0.0013671 | 56392.0495 | 0.023681 | 1.6956 | 39.8904 | 46.4362 | 4.3341 | 0.39088
2025-02-06 22:46 | 0.59225 | 0.67241 | 26.4066 | 0.055233 | 0.97873 | 0.65067 | 0.0014084 | 58096.3086 | 0.023681 | 1.6956 | 40.925 | 47.6405 | 4.4338 | 0.39987
2025-02-06 22:47 | 0.59958 | 0.68074 | 26.4066 | 0.05494 | 0.97873 | 0.65873 | 0.0014258 | 58815.885 | 0.023681 | 1.6956 | 41.3605 | 48.1476 | 4.462 | 0.40241
2025-02-06 22:48 | 0.59456 | 0.67504 | 26.4066 | 0.05453 | 0.97873 | 0.65321 | 0.0014139 | 58323.5451 | 0.023681 | 1.6956 | 41.0626 | 47.8008 | 4.3936 | 0.39625
2025-02-06 22:49 | 0.58762 | 0.66715 | 26.4066 | 0.054109 | 0.97873 | 0.64558 | 0.0013974 | 57641.842 | 0.023681 | 1.6956 | 40.6495 | 47.3199 | 4.3114 | 0.38883
2025-02-06 22:50 | 0.59495 | 0.67548 | 26.4066 | 0.053666 | 0.97873 | 0.65364 | 0.0014148 | 58361.4166 | 0.023681 | 1.6956 | 41.0855 | 47.8274 | 4.3266 | 0.3902
2025-02-06 22:51 | 0.60731 | 0.68951 | 26.4066 | 0.053392 | 0.97873 | 0.66721 | 0.0014442 | 59573.3329 | 0.023681 | 1.6956 | 41.8182 | 48.6803 | 4.389 | 0.39584
2025-02-06 22:52 | 0.6131 | 0.69608 | 26.4066 | 0.053087 | 0.97873 | 0.67357 | 0.0014579 | 60141.4201 | 0.023681 | 1.6956 | 42.1609 | 49.0793 | 4.4033 | 0.39713
2025-02-06 22:53 | 0.60229 | 0.68381 | 26.4066 | 0.052833 | 0.97873 | 0.66169 | 0.0014322 | 59080.993 | 0.023681 | 1.6956 | 41.5208 | 48.3341 | 4.3091 | 0.38863
2025-02-06 22:54 | 0.5965 | 0.67723 | 26.4066 | 0.052536 | 0.97873 | 0.65533 | 0.0014185 | 58512.9062 | 0.023681 | 1.6956 | 41.1772 | 47.9342 | 4.2458 | 0.38292
2025-02-06 22:55 | 0.59418 | 0.6746 | 26.4066 | 0.052254 | 0.97873 | 0.65279 | 0.001413 | 58285.6714 | 0.023681 | 1.6956 | 41.0397 | 47.7741 | 4.2076 | 0.37947
2025-02-06 22:56 | 0.60229 | 0.68381 | 26.4066 | 0.052067 | 0.97873 | 0.66169 | 0.0014322 | 59080.993 | 0.023681 | 1.6956 | 41.5208 | 48.3341 | 4.2466 | 0.38299
2025-02-06 22:57 | 0.59843 | 0.67942 | 26.4066 | 0.051811 | 0.97873 | 0.65745 | 0.0014231 | 58702.2691 | 0.023681 | 1.6956 | 41.2918 | 48.0676 | 4.2001 | 0.3788
2025-02-06 22:58 | 0.60267 | 0.68425 | 26.4065 | 0.051655 | 0.97873 | 0.66212 | 0.0014332 | 59118.8354 | 0.023681 | 1.6955 | 41.5437 | 48.3607 | 4.2156 | 0.38019
2025-02-06 22:59 | 0.60653 | 0.68863 | 26.406 | 0.051552 | 0.97873 | 0.66636 | 0.0014423 | 59497.3727 | 0.023681 | 1.6955 | 41.7725 | 48.6263 | 4.2326 | 0.38172
2025-02-06 23:00 | 0.59495 | 0.67547 | 26.4053 | 0.051345 | 0.97873 | 0.65364 | 0.0014148 | 58360.9993 | 0.023682 | 1.6955 | 41.0855 | 47.8259 | 4.1393 | 0.37331
2025-02-06 23:01 | 0.60151 | 0.68292 | 26.4047 | 0.051224 | 0.97874 | 0.66085 | 0.0014304 | 59004.6201 | 0.023682 | 1.6955 | 41.475 | 48.2786 | 4.1726 | 0.37632
2025-02-06 23:02 | 0.58955 | 0.66933 | 26.404 | 0.051135 | 0.97874 | 0.6477 | 0.0014019 | 57830.3865 | 0.023683 | 1.6954 | 40.7643 | 47.4506 | 4.0868 | 0.36858
2025-02-06 23:03 | 0.58839 | 0.66802 | 26.4035 | 0.051 | 0.97874 | 0.64642 | 0.0013992 | 57716.5879 | 0.023683 | 1.6954 | 40.6954 | 47.3698 | 4.0683 | 0.36691
2025-02-06 23:04 | 0.60731 | 0.68949 | 26.4032 | 0.050938 | 0.97874 | 0.66721 | 0.0014442 | 59572.2224 | 0.023683 | 1.6954 | 41.8182 | 48.6764 | 4.1869 | 0.37761
2025-02-06 23:05 | 0.59997 | 0.68116 | 26.403 | 0.050734 | 0.97874 | 0.65915 | 0.0014267 | 58852.5932 | 0.023684 | 1.6954 | 41.3834 | 48.1701 | 4.1224 | 0.37179
2025-02-06 23:06 | 0.61039 | 0.693 | 26.4028 | 0.050575 | 0.97874 | 0.6706 | 0.0014515 | 59875.0604 | 0.023684 | 1.6954 | 42.0011 | 48.8887 | 4.177 | 0.37671
2025-02-06 23:07 | 0.60808 | 0.69037 | 26.4026 | 0.050431 | 0.97874 | 0.66806 | 0.001446 | 59647.7618 | 0.023684 | 1.6954 | 41.8639 | 48.7288 | 4.1501 | 0.37429
2025-02-06 23:08 | 0.60653 | 0.68861 | 26.4024 | 0.050377 | 0.97874 | 0.66636 | 0.0014423 | 59496.2075 | 0.023684 | 1.6954 | 41.7725 | 48.6222 | 4.1357 | 0.37299
2025-02-06 23:09 | 0.59688 | 0.67765 | 26.4021 | 0.050218 | 0.97874 | 0.65576 | 0.0014194 | 58549.3503 | 0.023684 | 1.6953 | 41.2002 | 47.9557 | 4.0605 | 0.36621
2025-02-06 23:10 | 0.60808 | 0.69037 | 26.4019 | 0.050107 | 0.97874 | 0.66806 | 0.001446 | 59647.5545 | 0.023684 | 1.6953 | 41.8639 | 48.7281 | 4.1234 | 0.37188
2025-02-06 23:11 | 0.61039 | 0.69299 | 26.4017 | 0.05 | 0.97874 | 0.6706 | 0.0014515 | 59874.7138 | 0.023684 | 1.6953 | 42.0011 | 48.8875 | 4.1293 | 0.37242
2025-02-06 23:12 | 0.57526 | 0.65311 | 26.4015 | 0.04997 | 0.97874 | 0.632 | 0.001368 | 56428.3492 | 0.023685 | 1.6953 | 39.9134 | 46.4573 | 3.9017 | 0.35189
2025-02-06 23:13 | 0.55094 | 0.62549 | 26.4013 | 0.049857 | 0.97874 | 0.60528 | 0.0013101 | 54042.3825 | 0.023685 | 1.6953 | 38.4577 | 44.7627 | 3.7369 | 0.33702
2025-02-06 23:14 | 0.57565 | 0.65354 | 26.4008 | 0.049705 | 0.97874 | 0.63243 | 0.0013689 | 56466.0242 | 0.023685 | 1.6953 | 39.9365 | 46.4834 | 3.8834 | 0.35023
2025-02-06 23:15 | 0.58375 | 0.66275 | 26.4004 | 0.049616 | 0.97874 | 0.64134 | 0.0013882 | 57261.1877 | 0.023685 | 1.6953 | 40.4197 | 47.0454 | 3.9281 | 0.35427
2025-02-06 23:16 | 0.58762 | 0.66713 | 26.4 | 0.049422 | 0.97874 | 0.64558 | 0.0013974 | 57639.7649 | 0.023686 | 1.6953 | 40.6495 | 47.3124 | 3.9371 | 0.35508
2025-02-06 23:17 | 0.58916 | 0.66888 | 26.3996 | 0.049208 | 0.97875 | 0.64727 | 0.001401 | 57791.1147 | 0.023686 | 1.6952 | 40.7414 | 47.4188 | 3.9298 | 0.35442
2025-02-06 23:18 | 0.60113 | 0.68246 | 26.3991 | 0.04906 | 0.97875 | 0.66042 | 0.0014295 | 58964.952 | 0.023686 | 1.6952 | 41.4521 | 48.2455 | 3.9932 | 0.36014
2025-02-06 23:19 | 0.60808 | 0.69035 | 26.3981 | 0.048895 | 0.97875 | 0.66806 | 0.001446 | 59646.3069 | 0.023687 | 1.6952 | 41.8639 | 48.7236 | 4.0232 | 0.36284
2025-02-06 23:20 | 0.59341 | 0.67369 | 26.397 | 0.048661 | 0.97875 | 0.65194 | 0.0014111 | 58206.8843 | 0.023688 | 1.6951 | 40.9938 | 47.7097 | 3.9124 | 0.35285
2025-02-06 23:21 | 0.59148 | 0.6715 | 26.3959 | 0.048456 | 0.97875 | 0.64982 | 0.0014065 | 58017.1946 | 0.023689 | 1.6951 | 40.8791 | 47.575 | 3.8838 | 0.35027
2025-02-06 23:22 | 0.59688 | 0.67763 | 26.3948 | 0.048298 | 0.97876 | 0.65576 | 0.0014194 | 58547.0365 | 0.023689 | 1.695 | 41.2002 | 47.9474 | 3.9044 | 0.35213
2025-02-06 23:23 | 0.61541 | 0.69866 | 26.3938 | 0.048021 | 0.97876 | 0.67612 | 0.0014635 | 60364.4704 | 0.02369 | 1.695 | 42.2979 | 49.2238 | 3.9958 | 0.36038
2025-02-06 23:24 | 0.59997 | 0.68113 | 26.3933 | 0.047857 | 0.97876 | 0.65915 | 0.0014267 | 58849.5078 | 0.02369 | 1.695 | 41.3834 | 48.159 | 3.8876 | 0.35061
2025-02-06 23:25 | 0.60074 | 0.682 | 26.3928 | 0.04768 | 0.97876 | 0.66 | 0.0014286 | 58925.1011 | 0.023691 | 1.6949 | 41.4292 | 48.2118 | 3.8778 | 0.34973
2025-02-06 23:26 | 0.5907 | 0.67061 | 26.3924 | 0.047534 | 0.97876 | 0.64897 | 0.0014047 | 57940.3473 | 0.023691 | 1.6949 | 40.8332 | 47.5176 | 3.8048 | 0.34314
2025-02-06 23:27 | 0.60885 | 0.6912 | 26.3919 | 0.047391 | 0.97876 | 0.66891 | 0.0014478 | 59720.0654 | 0.023691 | 1.6949 | 41.9096 | 48.7698 | 3.9035 | 0.35204
2025-02-06 23:28 | 0.60962 | 0.69208 | 26.3915 | 0.047259 | 0.97876 | 0.66975 | 0.0014497 | 59795.6548 | 0.023692 | 1.6949 | 41.9554 | 48.8224 | 3.8972 | 0.35148
2025-02-06 23:29 | 0.59727 | 0.67805 | 26.391 | 0.04715 | 0.97876 | 0.65618 | 0.0014203 | 58583.6922 | 0.023692 | 1.6948 | 41.2231 | 47.9698 | 3.8136 | 0.34394
2025-02-06 23:30 | 0.57603 | 0.65394 | 26.3906 | 0.04701 | 0.97876 | 0.63285 | 0.0013698 | 56500.7524 | 0.023692 | 1.6948 | 39.9595 | 46.4989 | 3.6741 | 0.33136
2025-02-06 23:31 | 0.58646 | 0.66578 | 26.3903 | 0.046856 | 0.97876 | 0.6443 | 0.0013946 | 57523.142 | 0.023693 | 1.6948 | 40.5806 | 47.2214 | 3.7247 | 0.33592
2025-02-06 23:32 | 0.59688 | 0.67761 | 26.3901 | 0.046678 | 0.97876 | 0.65576 | 0.0014194 | 58545.5404 | 0.023693 | 1.6948 | 41.2002 | 47.9421 | 3.773 | 0.34028
2025-02-06 23:33 | 0.58337 | 0.66227 | 26.3899 | 0.046533 | 0.97877 | 0.64091 | 0.0013873 | 57220.0571 | 0.023693 | 1.6948 | 40.3967 | 47.0069 | 3.6806 | 0.33194
2025-02-06 23:34 | 0.59456 | 0.67498 | 26.3897 | 0.046345 | 0.97877 | 0.65321 | 0.0014139 | 58318.1906 | 0.023693 | 1.6948 | 41.0626 | 47.7815 | 3.7323 | 0.3366
2025-02-06 23:35 | 0.60113 | 0.68243 | 26.3894 | 0.046077 | 0.97877 | 0.66042 | 0.0014295 | 58961.8775 | 0.023693 | 1.6948 | 41.4521 | 48.2345 | 3.7494 | 0.33815
2025-02-06 23:36 | 0.61194 | 0.6947 | 26.3888 | 0.045969 | 0.97877 | 0.6723 | 0.0014552 | 60022.0142 | 0.023694 | 1.6948 | 42.0924 | 48.9789 | 3.8042 | 0.34309
2025-02-06 23:37 | 0.59881 | 0.67979 | 26.3882 | 0.045852 | 0.97877 | 0.65788 | 0.001424 | 58734.2718 | 0.023694 | 1.6947 | 41.3147 | 48.0732 | 3.7173 | 0.33526
2025-02-06 23:38 | 0.60499 | 0.68681 | 26.3875 | 0.045688 | 0.97877 | 0.66466 | 0.0014387 | 59339.963 | 0.023694 | 1.6947 | 41.681 | 48.4986 | 3.7401 | 0.33731
2025-02-06 23:39 | 0.60229 | 0.68373 | 26.3869 | 0.045599 | 0.97877 | 0.66169 | 0.0014322 | 59074.6764 | 0.023695 | 1.6947 | 41.5208 | 48.3115 | 3.717 | 0.33523
2025-02-06 23:40 | 0.59843 | 0.67935 | 26.3863 | 0.045538 | 0.97877 | 0.65745 | 0.0014231 | 58695.7883 | 0.023695 | 1.6946 | 41.2918 | 48.0443 | 3.6894 | 0.33274
2025-02-06 23:41 | 0.60653 | 0.68855 | 26.3856 | 0.045423 | 0.97877 | 0.66636 | 0.0014423 | 59490.8144 | 0.023696 | 1.6946 | 41.7725 | 48.6029 | 3.7272 | 0.33614
2025-02-06 23:42 | 0.60422 | 0.68592 | 26.385 | 0.045248 | 0.97878 | 0.66382 | 0.0014368 | 59263.3979 | 0.023696 | 1.6946 | 41.6352 | 48.4424 | 3.6993 | 0.33363
2025-02-06 23:43 | 0.588 | 0.66751 | 26.3843 | 0.045102 | 0.97878 | 0.646 | 0.0013983 | 57672.742 | 0.023697 | 1.6946 | 40.6725 | 47.3215 | 3.5937 | 0.3241
2025-02-06 23:44 | 0.61271 | 0.69556 | 26.3837 | 0.044982 | 0.97878 | 0.67315 | 0.001457 | 60096.0758 | 0.023697 | 1.6945 | 42.1381 | 49.026 | 3.7263 | 0.33607
2025-02-06 23:45 | 0.62661 | 0.71133 | 26.3831 | 0.044962 | 0.97878 | 0.68842 | 0.0014901 | 61459.1158 | 0.023698 | 1.6945 | 42.9589 | 49.9802 | 3.8046 | 0.34312
2025-02-06 23:46 | 0.61348 | 0.69643 | 26.3828 | 0.045017 | 0.97878 | 0.674 | 0.0014589 | 60171.5315 | 0.023698 | 1.6945 | 42.1838 | 49.0781 | 3.7336 | 0.33673
2025-02-06 23:47 | 0.58762 | 0.66706 | 26.3826 | 0.044977 | 0.97878 | 0.64558 | 0.0013974 | 57634.3401 | 0.023698 | 1.6945 | 40.6495 | 47.2929 | 3.5812 | 0.32298
2025-02-06 23:48 | 0.6046 | 0.68635 | 26.3824 | 0.044951 | 0.97878 | 0.66424 | 0.0014377 | 59300.4396 | 0.023698 | 1.6945 | 41.6581 | 48.4661 | 3.677 | 0.33162
2025-02-06 23:49 | 0.62082 | 0.70475 | 26.3822 | 0.044983 | 0.97878 | 0.68205 | 0.0014763 | 60890.8005 | 0.023698 | 1.6945 | 42.6172 | 49.5816 | 3.7729 | 0.34027
2025-02-06 23:50 | 0.59186 | 0.67188 | 26.3818 | 0.045019 | 0.97878 | 0.65024 | 0.0014075 | 58050.6348 | 0.023699 | 1.6944 | 40.902 | 47.5858 | 3.609 | 0.32549
2025-02-06 23:51 | 0.57256 | 0.64996 | 26.3807 | 0.045077 | 0.97878 | 0.62903 | 0.0013615 | 56156.9177 | 0.023699 | 1.6944 | 39.7521 | 46.2467 | 3.5019 | 0.31583
2025-02-06 23:52 | 0.60422 | 0.6859 | 26.3794 | 0.044947 | 0.97879 | 0.66382 | 0.0014368 | 59261.6091 | 0.0237 | 1.6943 | 41.6352 | 48.436 | 3.6742 | 0.33137
2025-02-06 23:53 | 0.59341 | 0.67362 | 26.3781 | 0.044904 | 0.97879 | 0.65194 | 0.0014111 | 58200.9314 | 0.023701 | 1.6943 | 40.9938 | 47.6884 | 3.6084 | 0.32543
2025-02-06 23:54 | 0.60151 | 0.68282 | 26.3768 | 0.044791 | 0.97879 | 0.66085 | 0.0014304 | 58995.7173 | 0.023702 | 1.6942 | 41.475 | 48.2467 | 3.6456 | 0.32879
2025-02-06 23:55 | 0.62391 | 0.70824 | 26.3756 | 0.044761 | 0.97879 | 0.68545 | 0.0014837 | 61191.5725 | 0.023703 | 1.6942 | 42.7995 | 49.786 | 3.7712 | 0.34012
2025-02-06 23:56 | 0.60229 | 0.68369 | 26.3751 | 0.044781 | 0.9788 | 0.66169 | 0.0014322 | 59070.8919 | 0.023703 | 1.6941 | 41.5208 | 48.298 | 3.6491 | 0.3291
2025-02-06 23:57 | 0.61194 | 0.69465 | 26.3746 | 0.044772 | 0.9788 | 0.6723 | 0.0014552 | 60017.3914 | 0.023704 | 1.6941 | 42.0924 | 48.9623 | 3.7036 | 0.33401
2025-02-06 23:58 | 0.61773 | 0.70122 | 26.3741 | 0.04476 | 0.9788 | 0.67866 | 0.001469 | 60585.2293 | 0.023704 | 1.6941 | 42.4348 | 49.36 | 3.7357 | 0.33691
2025-02-06 23:59 | 0.60692 | 0.68894 | 26.3737 | 0.044592 | 0.9788 | 0.66678 | 0.0014433 | 59524.8407 | 0.023704 | 1.6941 | 41.7953 | 48.6157 | 3.66 | 0.33008
2025-02-07 | 0.60499 | 0.68675 | 26.3732 | 0.044714 | 0.9788 | 0.66466 | 0.0014387 | 59335.364 | 0.023705 | 1.6941 | 41.681 | 48.4822 | 3.6589 | 0.32998
2025-02-07 00:01 | 0.60615 | 0.68806 | 26.3728 | 0.044512 | 0.9788 | 0.66594 | 0.0014414 | 59448.8114 | 0.023705 | 1.694 | 41.7496 | 48.5615 | 3.6489 | 0.32908
2025-02-07 00:02 | 0.59225 | 0.67229 | 26.3723 | 0.044475 | 0.9788 | 0.65067 | 0.0014084 | 58085.5016 | 0.023705 | 1.694 | 40.925 | 47.6017 | 3.5666 | 0.32166
2025-02-07 00:03 | 0.57294 | 0.65037 | 26.3717 | 0.044473 | 0.9788 | 0.62946 | 0.0013625 | 56192.0445 | 0.023706 | 1.694 | 39.7752 | 46.2636 | 3.4563 | 0.31172
2025-02-07 00:04 | 0.60113 | 0.68236 | 26.371 | 0.044373 | 0.9788 | 0.66042 | 0.0014295 | 58956.0037 | 0.023706 | 1.694 | 41.4521 | 48.2135 | 3.6088 | 0.32547
2025-02-07 00:05 | 0.61966 | 0.70339 | 26.3704 | 0.044366 | 0.9788 | 0.68078 | 0.0014736 | 60773.3166 | 0.023707 | 1.6939 | 42.5488 | 49.4882 | 3.7133 | 0.33489
2025-02-07 00:06 | 0.60769 | 0.68981 | 26.3697 | 0.044366 | 0.97881 | 0.66763 | 0.0014451 | 59599.2939 | 0.023707 | 1.6939 | 41.8411 | 48.6643 | 3.6453 | 0.32876
2025-02-07 00:07 | 0.60808 | 0.69024 | 26.3691 | 0.044388 | 0.97881 | 0.66806 | 0.001446 | 59636.9592 | 0.023708 | 1.6939 | 41.8639 | 48.6902 | 3.6493 | 0.32912
2025-02-07 00:08 | 0.61619 | 0.69944 | 26.3686 | 0.044467 | 0.97881 | 0.67696 | 0.0014653 | 60431.9612 | 0.023708 | 1.6938 | 42.3435 | 49.2474 | 3.7019 | 0.33386
2025-02-07 00:09 | 0.60267 | 0.6841 | 26.3682 | 0.044529 | 0.97881 | 0.66212 | 0.0014332 | 59106.5522 | 0.023708 | 1.6938 | 41.5437 | 48.3167 | 3.63 | 0.32738
2025-02-07 00:10 | 0.5992 | 0.68016 | 26.3677 | 0.044577 | 0.97881 | 0.6583 | 0.0014249 | 58765.6242 | 0.023709 | 1.6938 | 41.3376 | 48.0765 | 3.614 | 0.32594
2025-02-07 00:11 | 0.62661 | 0.71127 | 26.3673 | 0.044513 | 0.97881 | 0.68842 | 0.0014901 | 61453.8454 | 0.023709 | 1.6938 | 42.9589 | 49.9615 | 3.7649 | 0.33954
2025-02-07 00:12 | 0.61348 | 0.69637 | 26.3668 | 0.04452 | 0.97881 | 0.674 | 0.0014589 | 60166.3093 | 0.023709 | 1.6938 | 42.1838 | 49.0595 | 3.6907 | 0.33285
2025-02-07 00:13 | 0.59148 | 0.67139 | 26.3663 | 0.044576 | 0.97881 | 0.64982 | 0.0014065 | 58007.9029 | 0.023709 | 1.6937 | 40.8791 | 47.5416 | 3.5698 | 0.32195
2025-02-07 00:14 | 0.61773 | 0.70119 | 26.3659 | 0.044714 | 0.97881 | 0.67866 | 0.001469 | 60582.5248 | 0.02371 | 1.6937 | 42.4348 | 49.3504 | 3.7309 | 0.33648
2025-02-07 00:15 | 0.61039 | 0.69286 | 26.3657 | 0.044946 | 0.97881 | 0.6706 | 0.0014515 | 59863.0284 | 0.02371 | 1.6937 | 42.0011 | 48.8457 | 3.7081 | 0.33443
2025-02-07 00:16 | 0.59688 | 0.67752 | 26.3654 | 0.045017 | 0.97881 | 0.65576 | 0.0014194 | 58537.7186 | 0.02371 | 1.6937 | 41.2002 | 47.914 | 3.6362 | 0.32794
2025-02-07 00:17 | 0.63858 | 0.72485 | 26.3652 | 0.04501 | 0.97882 | 0.70157 | 0.0015185 | 62626.9547 | 0.02371 | 1.6937 | 43.6636 | 50.7786 | 3.8754 | 0.34951
2025-02-07 00:18 | 0.63626 | 0.72222 | 26.365 | 0.045098 | 0.97882 | 0.69902 | 0.001513 | 62399.6987 | 0.02371 | 1.6937 | 43.5273 | 50.6199 | 3.8696 | 0.34899
2025-02-07 00:19 | 0.61001 | 0.69242 | 26.3647 | 0.045171 | 0.97882 | 0.67018 | 0.0014506 | 59824.8502 | 0.023711 | 1.6937 | 41.9782 | 48.818 | 3.7244 | 0.3359
2025-02-07 00:20 | 0.57101 | 0.64815 | 26.3637 | 0.045176 | 0.97882 | 0.62734 | 0.0013579 | 56000.311 | 0.023711 | 1.6936 | 39.6599 | 46.1209 | 3.499 | 0.31556
2025-02-07 00:21 | 0.53318 | 0.6052 | 26.3627 | 0.045143 | 0.97882 | 0.58577 | 0.0012679 | 52289.3729 | 0.023712 | 1.6936 | 37.3891 | 43.4791 | 3.2765 | 0.2955
2025-02-07 00:22 | 0.5104 | 0.57934 | 26.3616 | 0.045018 | 0.97882 | 0.56074 | 0.0012137 | 50055.14 | 0.023713 | 1.6935 | 36.0112 | 41.8757 | 3.1349 | 0.28273
2025-02-07 00:23 | 0.50692 | 0.57539 | 26.3605 | 0.044943 | 0.97882 | 0.55693 | 0.0012055 | 49714.0814 | 0.023714 | 1.6935 | 35.8003 | 41.6293 | 3.1094 | 0.28043
2025-02-07 00:24 | 0.50191 | 0.56969 | 26.3595 | 0.044938 | 0.97883 | 0.55141 | 0.0011935 | 49221.593 | 0.023714 | 1.6934 | 35.4952 | 41.2736 | 3.0798 | 0.27776
2025-02-07 00:25 | 0.49882 | 0.56619 | 26.3588 | 0.044916 | 0.97883 | 0.54802 | 0.0011862 | 48918.5065 | 0.023715 | 1.6934 | 35.3073 | 41.0544 | 3.0603 | 0.276
2025-02-07 00:26 | 0.50384 | 0.57188 | 26.3581 | 0.044792 | 0.97883 | 0.55353 | 0.0011981 | 49410.547 | 0.023715 | 1.6934 | 35.6126 | 41.4088 | 3.0808 | 0.27785
2025-02-07 00:27 | 0.50152 | 0.56925 | 26.3575 | 0.04456 | 0.97883 | 0.55099 | 0.0011926 | 49183.2005 | 0.023716 | 1.6933 | 35.4717 | 41.2444 | 3.0515 | 0.27521
2025-02-07 00:28 | 0.50577 | 0.57407 | 26.3569 | 0.044311 | 0.97883 | 0.55565 | 0.0012027 | 49599.5144 | 0.023716 | 1.6933 | 35.7299 | 41.5439 | 3.0587 | 0.27586
2025-02-07 00:29 | 0.49071 | 0.55698 | 26.3563 | 0.043994 | 0.97883 | 0.53911 | 0.0011669 | 48122.7484 | 0.023717 | 1.6933 | 34.8132 | 40.4775 | 2.951 | 0.26615
2025-02-07 00:30 | 0.47527 | 0.53945 | 26.3564 | 0.043594 | 0.97883 | 0.52215 | 0.0011302 | 46608.2902 | 0.023716 | 1.6933 | 33.8689 | 39.3796 | 2.8369 | 0.25585
2025-02-07 00:31 | 0.46677 | 0.52981 | 26.3566 | 0.043278 | 0.97883 | 0.51281 | 0.00111 | 45775.3751 | 0.023716 | 1.6933 | 33.3477 | 38.7738 | 2.7686 | 0.24969
2025-02-07 00:32 | 0.46059 | 0.5228 | 26.3569 | 0.04309 | 0.97883 | 0.50603 | 0.0010953 | 45169.6329 | 0.023716 | 1.6933 | 32.9678 | 38.3323 | 2.722 | 0.24549
2025-02-07 00:33 | 0.45944 | 0.52148 | 26.3571 | 0.043056 | 0.97883 | 0.50475 | 0.0010925 | 45056.1 | 0.023716 | 1.6933 | 32.8965 | 38.2496 | 2.7134 | 0.24471
2025-02-07 00:34 | 0.46175 | 0.52411 | 26.3572 | 0.042976 | 0.97883 | 0.5073 | 0.0010981 | 45283.2997 | 0.023716 | 1.6933 | 33.0391 | 38.4155 | 2.7213 | 0.24543
2025-02-07 00:35 | 0.47835 | 0.54295 | 26.3566 | 0.042904 | 0.97883 | 0.52554 | 0.0011375 | 46911.2413 | 0.023716 | 1.6933 | 34.0581 | 39.5998 | 2.8092 | 0.25336
2025-02-07 00:36 | 0.48839 | 0.55435 | 26.356 | 0.042777 | 0.97883 | 0.53657 | 0.0011614 | 47895.4923 | 0.023717 | 1.6933 | 34.6718 | 40.3128 | 2.8565 | 0.25762
2025-02-07 00:37 | 0.47951 | 0.54427 | 26.3554 | 0.042701 | 0.97884 | 0.52681 | 0.0011403 | 47024.5016 | 0.023717 | 1.6933 | 34.129 | 39.6811 | 2.8023 | 0.25273
2025-02-07 00:38 | 0.47681 | 0.5412 | 26.3547 | 0.042686 | 0.97884 | 0.52384 | 0.0011339 | 46759.3039 | 0.023718 | 1.6932 | 33.9635 | 39.488 | 2.7862 | 0.25128
2025-02-07 00:39 | 0.4938 | 0.56048 | 26.3541 | 0.04264 | 0.97884 | 0.5425 | 0.0011743 | 48425.0683 | 0.023718 | 1.6932 | 35.0016 | 40.6944 | 2.8771 | 0.25948
2025-02-07 00:40 | 0.49303 | 0.5596 | 26.3539 | 0.04257 | 0.97884 | 0.54166 | 0.0011724 | 48349.2753 | 0.023718 | 1.6932 | 34.9545 | 40.6394 | 2.8681 | 0.25867
2025-02-07 00:41 | 0.49573 | 0.56266 | 26.3536 | 0.042488 | 0.97884 | 0.54463 | 0.0011788 | 48614.2486 | 0.023718 | 1.6932 | 35.1192 | 40.8307 | 2.8774 | 0.25951
2025-02-07 00:42 | 0.49573 | 0.56266 | 26.3534 | 0.042504 | 0.97884 | 0.54463 | 0.0011788 | 48614.1922 | 0.023719 | 1.6932 | 35.1192 | 40.8305 | 2.8785 | 0.25961
2025-02-07 00:43 | 0.4938 | 0.56047 | 26.3532 | 0.042406 | 0.97884 | 0.5425 | 0.0011743 | 48424.8295 | 0.023719 | 1.6932 | 35.0016 | 40.6935 | 2.8612 | 0.25805
2025-02-07 00:44 | 0.49689 | 0.56398 | 26.353 | 0.042521 | 0.97884 | 0.5459 | 0.0011816 | 48727.6649 | 0.023719 | 1.6931 | 35.1898 | 40.9121 | 2.886 | 0.26028
2025-02-07 00:45 | 0.50113 | 0.5688 | 26.3528 | 0.042585 | 0.97884 | 0.55056 | 0.0011917 | 49144.0819 | 0.023719 | 1.6931 | 35.4483 | 41.2124 | 2.9138 | 0.26278
2025-02-07 00:46 | 0.48222 | 0.54732 | 26.3526 | 0.042545 | 0.97884 | 0.52978 | 0.0011467 | 47288.8197 | 0.023719 | 1.6931 | 34.2943 | 39.8707 | 2.8067 | 0.25313
2025-02-07 00:47 | 0.46716 | 0.53023 | 26.3524 | 0.042508 | 0.97884 | 0.51324 | 0.0011109 | 45812.1741 | 0.023719 | 1.6931 | 33.3714 | 38.7974 | 2.7212 | 0.24542
2025-02-07 00:48 | 0.46098 | 0.52322 | 26.3521 | 0.042495 | 0.97884 | 0.50645 | 0.0010962 | 45206.3413 | 0.02372 | 1.6931 | 32.9915 | 38.3556 | 2.6862 | 0.24226
2025-02-07 00:49 | 0.45249 | 0.51358 | 26.352 | 0.042427 | 0.97884 | 0.49712 | 0.001076 | 44373.3558 | 0.02372 | 1.6931 | 32.4681 | 37.7469 | 2.635 | 0.23764
2025-02-07 00:50 | 0.47681 | 0.54119 | 26.3521 | 0.042289 | 0.97884 | 0.52384 | 0.0011339 | 46758.6523 | 0.02372 | 1.6931 | 33.9635 | 39.4856 | 2.7601 | 0.24893
2025-02-07 00:51 | 0.4938 | 0.56047 | 26.3524 | 0.042246 | 0.97884 | 0.5425 | 0.0011743 | 48424.6045 | 0.023719 | 1.6931 | 35.0016 | 40.6927 | 2.8504 | 0.25707
2025-02-07 00:52 | 0.4853 | 0.55083 | 26.3526 | 0.042411 | 0.97884 | 0.53317 | 0.0011541 | 47591.7123 | 0.023719 | 1.6931 | 34.4832 | 40.0902 | 2.8148 | 0.25386
2025-02-07 00:53 | 0.46947 | 0.53286 | 26.3528 | 0.042322 | 0.97884 | 0.51578 | 0.0011164 | 46039.4491 | 0.023719 | 1.6931 | 33.5136 | 38.9632 | 2.722 | 0.24549
2025-02-07 00:54 | 0.46832 | 0.53155 | 26.353 | 0.042293 | 0.97884 | 0.51451 | 0.0011137 | 45925.9168 | 0.023719 | 1.6931 | 33.4425 | 38.8807 | 2.7138 | 0.24475
2025-02-07 00:55 | 0.47411 | 0.53812 | 26.3532 | 0.042191 | 0.97884 | 0.52087 | 0.0011274 | 46493.893 | 0.023719 | 1.6932 | 33.7979 | 39.2941 | 2.739 | 0.24703
2025-02-07 00:56 | 0.46909 | 0.53243 | 26.3534 | 0.042039 | 0.97884 | 0.51536 | 0.0011155 | 46001.7485 | 0.023719 | 1.6932 | 33.4899 | 38.9363 | 2.7018 | 0.24367
2025-02-07 00:57 | 0.49071 | 0.55697 | 26.3536 | 0.041929 | 0.97884 | 0.53911 | 0.0011669 | 48122.0497 | 0.023718 | 1.6932 | 34.8132 | 40.4749 | 2.8123 | 0.25364
2025-02-07 00:58 | 0.49997 | 0.56749 | 26.3539 | 0.042 | 0.97884 | 0.54929 | 0.0011889 | 49030.7836 | 0.023718 | 1.6932 | 35.3778 | 41.1316 | 2.8675 | 0.25861
2025-02-07 00:59 | 0.48646 | 0.55215 | 26.354 | 0.04195 | 0.97884 | 0.53445 | 0.0011568 | 47705.6549 | 0.023718 | 1.6932 | 34.5539 | 40.1738 | 2.7906 | 0.25168
2025-02-07 01:00 | 0.47488 | 0.539 | 26.3534 | 0.04199 | 0.97884 | 0.52172 | 0.0011293 | 46569.6701 | 0.023719 | 1.6932 | 33.8452 | 39.3493 | 2.7302 | 0.24623
2025-02-07 01:01 | 0.46059 | 0.52279 | 26.3528 | 0.042038 | 0.97884 | 0.50603 | 0.0010953 | 45168.6363 | 0.023719 | 1.6931 | 32.9678 | 38.3286 | 2.6552 | 0.23947
2025-02-07 01:02 | 0.45558 | 0.51709 | 26.3521 | 0.042063 | 0.97884 | 0.50051 | 0.0010834 | 44676.2843 | 0.02372 | 1.6931 | 32.6586 | 37.9686 | 2.6293 | 0.23713
2025-02-07 01:03 | 0.43704 | 0.49605 | 26.3515 | 0.042098 | 0.97884 | 0.48015 | 0.0010393 | 42858.7947 | 0.02372 | 1.6931 | 31.5128 | 36.6359 | 2.5298 | 0.22816
2025-02-07 01:04 | 0.42623 | 0.48378 | 26.351 | 0.042368 | 0.97884 | 0.46828 | 0.0010136 | 41798.5725 | 0.02372 | 1.6931 | 30.8413 | 35.8548 | 2.4861 | 0.22422
2025-02-07 01:05 | 0.43782 | 0.49693 | 26.3515 | 0.042498 | 0.97884 | 0.481 | 0.0010411 | 42934.5161 | 0.02372 | 1.6931 | 31.5607 | 36.6916 | 2.5581 | 0.23071
2025-02-07 01:06 | 0.44438 | 0.50438 | 26.3521 | 0.042283 | 0.97884 | 0.48821 | 0.0010567 | 43578.308 | 0.02372 | 1.6931 | 31.9671 | 37.1647 | 2.5814 | 0.23281
2025-02-07 01:07 | 0.43473 | 0.49343 | 26.3528 | 0.042334 | 0.97884 | 0.47761 | 0.0010338 | 42631.9247 | 0.023719 | 1.6931 | 31.3691 | 36.4699 | 2.5313 | 0.22829
2025-02-07 01:08 | 0.4382 | 0.49737 | 26.3534 | 0.042105 | 0.97884 | 0.48143 | 0.001042 | 42972.8256 | 0.023719 | 1.6932 | 31.5846 | 36.7211 | 2.5367 | 0.22878
2025-02-07 01:09 | 0.42778 | 0.48554 | 26.3539 | 0.041977 | 0.97884 | 0.46997 | 0.0010173 | 41950.6799 | 0.023718 | 1.6932 | 30.9373 | 35.969 | 2.4719 | 0.22294
2025-02-07 01:10 | 0.42276 | 0.47984 | 26.3536 | 0.041903 | 0.97884 | 0.46446 | 0.0010053 | 41458.414 | 0.023718 | 1.6932 | 30.6249 | 35.6055 | 2.44 | 0.22006
2025-02-07 01:11 | 0.41542 | 0.47152 | 26.3532 | 0.04182 | 0.97884 | 0.4564 | 0.00098788 | 40738.9498 | 0.023719 | 1.6932 | 30.1674 | 35.0732 | 2.3951 | 0.216
2025-02-07 01:12 | 0.39573 | 0.44917 | 26.3528 | 0.04187 | 0.97884 | 0.43477 | 0.00094106 | 38807.9245 | 0.023719 | 1.6931 | 28.9335 | 33.6383 | 2.2899 | 0.20652
2025-02-07 01:13 | 0.39457 | 0.44785 | 26.3524 | 0.041907 | 0.97884 | 0.43349 | 0.0009383 | 38694.2501 | 0.023719 | 1.6931 | 28.8607 | 33.5533 | 2.2855 | 0.20612
2025-02-07 01:14 | 0.38917 | 0.44171 | 26.3519 | 0.042121 | 0.97884 | 0.42756 | 0.00092545 | 38164.1012 | 0.02372 | 1.6931 | 28.5203 | 33.1573 | 2.2672 | 0.20448
2025-02-07 01:15 | 0.39689 | 0.45048 | 26.3515 | 0.04217 | 0.97884 | 0.43604 | 0.00094381 | 38921.2362 | 0.02372 | 1.6931 | 29.0063 | 33.722 | 2.3126 | 0.20856
2025-02-07 01:16 | 0.39612 | 0.4496 | 26.3511 | 0.042228 | 0.97884 | 0.43519 | 0.00094197 | 38845.4245 | 0.02372 | 1.6931 | 28.9578 | 33.6652 | 2.3114 | 0.20846
2025-02-07 01:17 | 0.38183 | 0.43339 | 26.3506 | 0.042432 | 0.97884 | 0.4195 | 0.000908 | 37444.4789 | 0.023721 | 1.693 | 28.0574 | 32.6181 | 2.243 | 0.20229
2025-02-07 01:18 | 0.37488 | 0.4255 | 26.3502 | 0.042535 | 0.97885 | 0.41186 | 0.00089148 | 36762.8974 | 0.023721 | 1.693 | 27.6177 | 32.1066 | 2.2095 | 0.19927
2025-02-07 01:19 | 0.34979 | 0.39701 | 26.3498 | 0.042453 | 0.97885 | 0.38429 | 0.0008318 | 34301.8561 | 0.023721 | 1.693 | 26.0201 | 30.249 | 2.0647 | 0.18621
2025-02-07 01:20 | 0.34902 | 0.39613 | 26.3491 | 0.042257 | 0.97885 | 0.38344 | 0.00082996 | 34226.0196 | 0.023722 | 1.693 | 25.9707 | 30.1911 | 2.0508 | 0.18496
2025-02-07 01:21 | 0.37064 | 0.42067 | 26.3485 | 0.042188 | 0.97885 | 0.4072 | 0.00088138 | 36346.0895 | 0.023722 | 1.6929 | 27.3484 | 31.7922 | 2.1678 | 0.19551
2025-02-07 01:22 | 0.37064 | 0.42067 | 26.3478 | 0.042306 | 0.97885 | 0.4072 | 0.00088138 | 36345.963 | 0.023723 | 1.6929 | 27.3484 | 31.7918 | 2.1738 | 0.19605
2025-02-07 01:23 | 0.36678 | 0.41629 | 26.3472 | 0.042504 | 0.97885 | 0.40296 | 0.0008722 | 35967.2343 | 0.023723 | 1.6929 | 27.1032 | 31.5063 | 2.1623 | 0.19501
2025-02-07 01:24 | 0.344 | 0.39043 | 26.3467 | 0.042284 | 0.97885 | 0.37793 | 0.00081803 | 33733.3822 | 0.023723 | 1.6929 | 25.6492 | 29.8156 | 2.0239 | 0.18253
2025-02-07 01:25 | 0.33898 | 0.38474 | 26.3468 | 0.04229 | 0.97885 | 0.37242 | 0.00080609 | 33241.2194 | 0.023723 | 1.6929 | 25.327 | 29.4412 | 1.9961 | 0.18002
2025-02-07 01:26 | 0.36214 | 0.41103 | 26.347 | 0.042403 | 0.97885 | 0.39787 | 0.00086118 | 35512.8696 | 0.023723 | 1.6929 | 26.8085 | 31.1635 | 2.1312 | 0.19221
2025-02-07 01:27 | 0.35481 | 0.4027 | 26.3472 | 0.042533 | 0.97885 | 0.38981 | 0.00084374 | 34793.5655 | 0.023723 | 1.6929 | 26.3409 | 30.6201 | 2.0966 | 0.18909
2025-02-07 01:28 | 0.35404 | 0.40183 | 26.3474 | 0.042486 | 0.97885 | 0.38896 | 0.0008419 | 34717.8854 | 0.023723 | 1.6929 | 26.2916 | 30.5629 | 2.09 | 0.18849
2025-02-07 01:29 | 0.36446 | 0.41366 | 26.3475 | 0.042471 | 0.97885 | 0.40041 | 0.00086669 | 35740.1244 | 0.023723 | 1.6929 | 26.956 | 31.3353 | 2.1477 | 0.19369
2025-02-07 01:30 | 0.36948 | 0.41935 | 26.3466 | 0.042626 | 0.97885 | 0.40592 | 0.00087862 | 36232.1307 | 0.023723 | 1.6929 | 27.2749 | 31.7053 | 2.1836 | 0.19694
2025-02-07 01:31 | 0.35558 | 0.40358 | 26.3455 | 0.042548 | 0.97886 | 0.39065 | 0.00084557 | 34868.9633 | 0.023724 | 1.6928 | 26.3902 | 30.6761 | 2.1016 | 0.18954
2025-02-07 01:32 | 0.34361 | 0.38999 | 26.3444 | 0.042419 | 0.97886 | 0.37751 | 0.00081711 | 33695.1109 | 0.023725 | 1.6928 | 25.6244 | 29.7853 | 2.0281 | 0.18291
2025-02-07 01:33 | 0.33821 | 0.38385 | 26.3433 | 0.042533 | 0.97886 | 0.37157 | 0.00080426 | 33164.8835 | 0.023726 | 1.6927 | 25.2774 | 29.3811 | 2.003 | 0.18065
2025-02-07 01:34 | 0.34979 | 0.397 | 26.3424 | 0.042586 | 0.97886 | 0.38429 | 0.0008318 | 34300.4977 | 0.023726 | 1.6927 | 26.0201 | 30.2438 | 2.0707 | 0.18675
2025-02-07 01:35 | 0.36021 | 0.40883 | 26.3425 | 0.042823 | 0.97886 | 0.39574 | 0.00085659 | 35322.7076 | 0.023726 | 1.6927 | 26.6856 | 31.0173 | 2.1412 | 0.19311
2025-02-07 01:36 | 0.35983 | 0.40839 | 26.3427 | 0.042784 | 0.97886 | 0.39532 | 0.00085567 | 35284.8889 | 0.023726 | 1.6927 | 26.661 | 30.9889 | 2.1371 | 0.19274
2025-02-07 01:37 | 0.35906 | 0.40751 | 26.3429 | 0.042602 | 0.97886 | 0.39447 | 0.00085384 | 35209.2115 | 0.023726 | 1.6927 | 26.6118 | 30.9318 | 2.1236 | 0.19153
2025-02-07 01:38 | 0.33705 | 0.38254 | 26.3431 | 0.042634 | 0.97886 | 0.37029 | 0.0008015 | 33051.2658 | 0.023726 | 1.6927 | 25.2029 | 29.2944 | 2.0012 | 0.18048
2025-02-07 01:39 | 0.32315 | 0.36676 | 26.3432 | 0.042815 | 0.97886 | 0.35502 | 0.00076845 | 31688.3454 | 0.023726 | 1.6927 | 24.3065 | 28.2526 | 1.9308 | 0.17414
2025-02-07 01:40 | 0.33049 | 0.37509 | 26.3427 | 0.042594 | 0.97886 | 0.36308 | 0.0007859 | 32407.5809 | 0.023726 | 1.6927 | 24.7803 | 28.8029 | 1.9623 | 0.17697
2025-02-07 01:41 | 0.35404 | 0.40182 | 26.3421 | 0.042444 | 0.97886 | 0.38896 | 0.0008419 | 34716.8777 | 0.023727 | 1.6927 | 26.2916 | 30.559 | 2.0876 | 0.18827
2025-02-07 01:42 | 0.35867 | 0.40707 | 26.3414 | 0.04269 | 0.97886 | 0.39405 | 0.00085292 | 35171.066 | 0.023727 | 1.6926 | 26.5872 | 30.9021 | 2.1258 | 0.19172
2025-02-07 01:43 | 0.3633 | 0.41233 | 26.3408 | 0.04282 | 0.97886 | 0.39914 | 0.00086393 | 35625.2515 | 0.023728 | 1.6926 | 26.8823 | 31.2446 | 2.1583 | 0.19466
2025-02-07 01:44 | 0.36987 | 0.41978 | 26.3402 | 0.042717 | 0.97887 | 0.40635 | 0.00087954 | 36268.7378 | 0.023728 | 1.6926 | 27.2994 | 31.729 | 2.19 | 0.19751
2025-02-07 01:45 | 0.38299 | 0.43467 | 26.3399 | 0.042853 | 0.97887 | 0.42077 | 0.00091076 | 37555.8826 | 0.023728 | 1.6926 | 28.1306 | 32.6949 | 2.2711 | 0.20482
2025-02-07 01:46 | 0.37643 | 0.42722 | 26.3397 | 0.042819 | 0.97887 | 0.41356 | 0.00089515 | 36912.2396 | 0.023728 | 1.6925 | 27.7155 | 32.2123 | 2.2323 | 0.20132
2025-02-07 01:47 | 0.34631 | 0.39305 | 26.3395 | 0.042905 | 0.97887 | 0.38047 | 0.00082354 | 33959.2211 | 0.023728 | 1.6925 | 25.7977 | 29.9831 | 2.0663 | 0.18636
2025-02-07 01:48 | 0.34207 | 0.38823 | 26.3393 | 0.042945 | 0.97887 | 0.37581 | 0.00081344 | 33542.7371 | 0.023729 | 1.6925 | 25.5254 | 29.6665 | 2.0441 | 0.18435
2025-02-07 01:49 | 0.34747 | 0.39436 | 26.339 | 0.042892 | 0.97887 | 0.38175 | 0.00082629 | 34072.7071 | 0.023729 | 1.6925 | 25.8718 | 30.069 | 2.0722 | 0.18689
2025-02-07 01:50 | 0.35133 | 0.39874 | 26.3384 | 0.04294 | 0.97887 | 0.38599 | 0.00083547 | 34451.1817 | 0.023729 | 1.6925 | 26.1189 | 30.3557 | 2.0964 | 0.18907
2025-02-07 01:51 | 0.35095 | 0.3983 | 26.3378 | 0.042735 | 0.97887 | 0.38556 | 0.00083456 | 34413.2035 | 0.02373 | 1.6925 | 26.0942 | 30.3265 | 2.0842 | 0.18797
2025-02-07 01:52 | 0.35056 | 0.39786 | 26.3371 | 0.042695 | 0.97887 | 0.38514 | 0.00083364 | 34375.2264 | 0.02373 | 1.6924 | 26.0695 | 30.2973 | 2.08 | 0.18759
2025-02-07 01:53 | 0.35751 | 0.40575 | 26.3365 | 0.042439 | 0.97887 | 0.39278 | 0.00085016 | 35056.5513 | 0.023731 | 1.6924 | 26.5133 | 30.8127 | 2.1065 | 0.18998
2025-02-07 01:54 | 0.35597 | 0.40399 | 26.3359 | 0.042491 | 0.97887 | 0.39108 | 0.00084649 | 34905.019 | 0.023731 | 1.6924 | 26.4148 | 30.6978 | 2.1004 | 0.18943
2025-02-07 01:55 | 0.35558 | 0.40356 | 26.3361 | 0.042642 | 0.97887 | 0.39065 | 0.00084557 | 34867.183 | 0.023731 | 1.6924 | 26.3902 | 30.6692 | 2.1056 | 0.1899
2025-02-07 01:56 | 0.35326 | 0.40093 | 26.3363 | 0.042737 | 0.97887 | 0.38811 | 0.00084006 | 34640.0753 | 0.023731 | 1.6924 | 26.2422 | 30.4975 | 2.0973 | 0.18915
2025-02-07 01:57 | 0.36523 | 0.41451 | 26.3365 | 0.042598 | 0.97887 | 0.40126 | 0.00086853 | 35813.7151 | 0.023731 | 1.6924 | 27.0051 | 31.3842 | 2.1577 | 0.1946
2025-02-07 01:58 | 0.35906 | 0.4075 | 26.3367 | 0.042637 | 0.97887 | 0.39447 | 0.00085384 | 35208.0268 | 0.02373 | 1.6924 | 26.6118 | 30.9273 | 2.125 | 0.19165
2025-02-07 01:59 | 0.33126 | 0.37595 | 26.3368 | 0.042744 | 0.97887 | 0.36393 | 0.00078773 | 32482.27 | 0.02373 | 1.6924 | 24.8301 | 28.8567 | 1.9732 | 0.17796
2025-02-07 02:00 | 0.33049 | 0.37508 | 26.3366 | 0.04241 | 0.97887 | 0.36308 | 0.0007859 | 32406.5104 | 0.023731 | 1.6924 | 24.7803 | 28.7987 | 1.9534 | 0.17617
2025-02-07 02:01 | 0.34631 | 0.39304 | 26.3363 | 0.042454 | 0.97887 | 0.38047 | 0.00082354 | 33958.6348 | 0.023731 | 1.6924 | 25.7977 | 29.9808 | 2.0444 | 0.18438
2025-02-07 02:02 | 0.33821 | 0.38384 | 26.336 | 0.042423 | 0.97887 | 0.37157 | 0.00080426 | 33163.5624 | 0.023731 | 1.6924 | 25.2774 | 29.376 | 1.9974 | 0.18014
2025-02-07 02:03 | 0.33628 | 0.38165 | 26.3357 | 0.042217 | 0.97888 | 0.36945 | 0.00079967 | 32974.2173 | 0.023731 | 1.6924 | 25.1533 | 29.2315 | 1.9769 | 0.17829
2025-02-07 02:04 | 0.3355 | 0.38077 | 26.3354 | 0.041952 | 0.97888 | 0.3686 | 0.00079783 | 32898.4466 | 0.023731 | 1.6924 | 25.1036 | 29.1736 | 1.9602 | 0.17678
2025-02-07 02:05 | 0.344 | 0.39041 | 26.3351 | 0.042115 | 0.97888 | 0.37793 | 0.00081803 | 33731.2632 | 0.023732 | 1.6923 | 25.6492 | 29.8074 | 2.0151 | 0.18174
2025-02-07 02:06 | 0.34631 | 0.39304 | 26.3348 | 0.042364 | 0.97888 | 0.38047 | 0.00082354 | 33958.3608 | 0.023732 | 1.6923 | 25.7977 | 29.9798 | 2.04 | 0.18398
2025-02-07 02:07 | 0.34014 | 0.38603 | 26.3348 | 0.042491 | 0.97888 | 0.37369 | 0.00080885 | 33352.6316 | 0.023732 | 1.6923 | 25.4014 | 29.5193 | 2.0114 | 0.1814
2025-02-07 02:08 | 0.35056 | 0.39786 | 26.3348 | 0.042026 | 0.97888 | 0.38514 | 0.00083364 | 34374.7894 | 0.023732 | 1.6923 | 26.0695 | 30.2957 | 2.0473 | 0.18464
2025-02-07 02:09 | 0.36716 | 0.4167 | 26.3348 | 0.042255 | 0.97888 | 0.40338 | 0.00087312 | 36002.671 | 0.023732 | 1.6923 | 27.1278 | 31.5255 | 2.151 | 0.19399
2025-02-07 02:10 | 0.36755 | 0.41714 | 26.3348 | 0.04256 | 0.97888 | 0.4038 | 0.00087403 | 36040.5281 | 0.023732 | 1.6923 | 27.1523 | 31.554 | 2.1687 | 0.19559
2025-02-07 02:11 | 0.36253 | 0.41144 | 26.3348 | 0.042584 | 0.97888 | 0.39829 | 0.0008621 | 35548.3769 | 0.023732 | 1.6923 | 26.8331 | 31.1831 | 2.1418 | 0.19316
2025-02-07 02:12 | 0.35712 | 0.40531 | 26.3348 | 0.04242 | 0.97888 | 0.39235 | 0.00084924 | 35018.37 | 0.023732 | 1.6923 | 26.4887 | 30.7828 | 2.1032 | 0.18969
2025-02-07 02:13 | 0.33821 | 0.38383 | 26.3347 | 0.042459 | 0.97888 | 0.37157 | 0.00080426 | 33163.3324 | 0.023732 | 1.6923 | 25.2774 | 29.3751 | 1.999 | 0.18029
2025-02-07 02:14 | 0.33821 | 0.38383 | 26.3343 | 0.042484 | 0.97888 | 0.37157 | 0.00080426 | 33163.2638 | 0.023732 | 1.6923 | 25.2774 | 29.3748 | 2.0002 | 0.18039
2025-02-07 02:15 | 0.34014 | 0.38602 | 26.3339 | 0.042323 | 0.97888 | 0.37369 | 0.00080885 | 33352.4742 | 0.023732 | 1.6923 | 25.4014 | 29.5187 | 2.0034 | 0.18068
2025-02-07 02:16 | 0.34284 | 0.38909 | 26.3335 | 0.042591 | 0.97888 | 0.37666 | 0.00081528 | 33617.3985 | 0.023733 | 1.6923 | 25.5749 | 29.72 | 2.0313 | 0.1832
2025-02-07 02:17 | 0.35056 | 0.39785 | 26.333 | 0.042364 | 0.97888 | 0.38514 | 0.00083364 | 34374.4675 | 0.023733 | 1.6922 | 26.0695 | 30.2944 | 2.0636 | 0.18612
2025-02-07 02:18 | 0.35365 | 0.40136 | 26.3326 | 0.042354 | 0.97888 | 0.38853 | 0.00084098 | 34677.2401 | 0.023733 | 1.6922 | 26.2669 | 30.5235 | 2.0804 | 0.18763
2025-02-07 02:19 | 0.33319 | 0.37813 | 26.3319 | 0.04244 | 0.97888 | 0.36605 | 0.00079232 | 32670.6961 | 0.023734 | 1.6922 | 24.9545 | 28.9979 | 1.9698 | 0.17765
2025-02-07 02:20 | 0.3274 | 0.37156 | 26.3313 | 0.042473 | 0.97888 | 0.35969 | 0.00077855 | 32102.7277 | 0.023734 | 1.6922 | 24.581 | 28.5635 | 1.9387 | 0.17484
2025-02-07 02:21 | 0.34593 | 0.39259 | 26.3307 | 0.042603 | 0.97889 | 0.38005 | 0.00082262 | 33919.7446 | 0.023735 | 1.6921 | 25.7729 | 29.9481 | 2.0491 | 0.1848
2025-02-07 02:22 | 0.35095 | 0.39828 | 26.33 | 0.042487 | 0.97889 | 0.38556 | 0.00083456 | 34411.7635 | 0.023735 | 1.6921 | 26.0942 | 30.3209 | 2.0716 | 0.18684
2025-02-07 02:23 | 0.34284 | 0.38908 | 26.3294 | 0.042475 | 0.97889 | 0.37666 | 0.00081528 | 33616.6615 | 0.023736 | 1.6921 | 25.5749 | 29.7171 | 2.0255 | 0.18268
2025-02-07 02:24 | 0.3467 | 0.39346 | 26.329 | 0.042567 | 0.97889 | 0.3809 | 0.00082446 | 33995.1437 | 0.023736 | 1.6921 | 25.8224 | 30.0044 | 2.0516 | 0.18503
2025-02-07 02:25 | 0.34825 | 0.39521 | 26.3285 | 0.042325 | 0.97889 | 0.3826 | 0.00082813 | 34146.4901 | 0.023736 | 1.692 | 25.9213 | 30.119 | 2.0486 | 0.18475
2025-02-07 02:26 | 0.35056 | 0.39784 | 26.3281 | 0.042326 | 0.97889 | 0.38514 | 0.00083364 | 34373.5492 | 0.023737 | 1.692 | 26.0695 | 30.2909 | 2.0615 | 0.18592
2025-02-07 02:27 | 0.35365 | 0.40135 | 26.3277 | 0.042759 | 0.97889 | 0.38853 | 0.00084098 | 34676.3192 | 0.023737 | 1.692 | 26.2669 | 30.5199 | 2.1 | 0.1894
2025-02-07 02:28 | 0.33319 | 0.37812 | 26.3273 | 0.042768 | 0.97889 | 0.36605 | 0.00079232 | 32669.8734 | 0.023737 | 1.692 | 24.9545 | 28.9947 | 1.9847 | 0.179
2025-02-07 02:29 | 0.32547 | 0.36936 | 26.3272 | 0.042409 | 0.97889 | 0.35757 | 0.00077396 | 31912.742 | 0.023737 | 1.692 | 24.4563 | 28.4159 | 1.9246 | 0.17358
2025-02-07 02:30 | 0.3413 | 0.38732 | 26.3272 | 0.042329 | 0.97889 | 0.37496 | 0.0008116 | 33464.844 | 0.023737 | 1.692 | 25.4758 | 29.6004 | 2.0098 | 0.18126
2025-02-07 02:31 | 0.33859 | 0.38426 | 26.3272 | 0.042563 | 0.97889 | 0.37199 | 0.00080518 | 33199.8515 | 0.023737 | 1.692 | 25.3022 | 29.3987 | 2.0057 | 0.18089
2025-02-07 02:32 | 0.31968 | 0.36279 | 26.3272 | 0.042484 | 0.97889 | 0.35121 | 0.00076019 | 31344.9002 | 0.023737 | 1.692 | 24.0816 | 27.9805 | 1.8954 | 0.17094
2025-02-07 02:33 | 0.32161 | 0.36498 | 26.3272 | 0.042337 | 0.97889 | 0.35333 | 0.00076478 | 31534.1808 | 0.023737 | 1.692 | 24.2066 | 28.1257 | 1.8997 | 0.17133
2025-02-07 02:34 | 0.32431 | 0.36805 | 26.3272 | 0.042248 | 0.97889 | 0.3563 | 0.00077121 | 31799.1737 | 0.023737 | 1.692 | 24.3814 | 28.3289 | 1.9109 | 0.17234
2025-02-07 02:35 | 0.33203 | 0.37681 | 26.3272 | 0.042476 | 0.97889 | 0.36478 | 0.00078957 | 32556.28 | 0.023737 | 1.692 | 24.8798 | 28.9079 | 1.9646 | 0.17719
2025-02-07 02:36 | 0.3467 | 0.39346 | 26.3266 | 0.042374 | 0.97889 | 0.3809 | 0.00082446 | 33994.7066 | 0.023738 | 1.692 | 25.8224 | 30.0027 | 2.0422 | 0.18418
2025-02-07 02:37 | 0.34631 | 0.39302 | 26.3259 | 0.042487 | 0.97889 | 0.38047 | 0.00082354 | 33956.7324 | 0.023738 | 1.6919 | 25.7977 | 29.9735 | 2.0454 | 0.18447
2025-02-07 02:38 | 0.34786 | 0.39477 | 26.3253 | 0.042473 | 0.9789 | 0.38217 | 0.00082721 | 34108.0379 | 0.023739 | 1.6919 | 25.8966 | 30.0879 | 2.0533 | 0.18518
2025-02-07 02:39 | 0.35365 | 0.40134 | 26.3246 | 0.042542 | 0.9789 | 0.38853 | 0.00084098 | 34675.7533 | 0.023739 | 1.6919 | 26.2669 | 30.5177 | 2.0892 | 0.18842
2025-02-07 02:40 | 0.34284 | 0.38907 | 26.324 | 0.042593 | 0.9789 | 0.37666 | 0.00081528 | 33615.6843 | 0.023739 | 1.6918 | 25.5749 | 29.7133 | 2.0308 | 0.18316
2025-02-07 02:41 | 0.34863 | 0.39564 | 26.3236 | 0.042477 | 0.9789 | 0.38302 | 0.00082905 | 34183.4327 | 0.02374 | 1.6918 | 25.946 | 30.1441 | 2.0578 | 0.18559
2025-02-07 02:42 | 0.35481 | 0.40265 | 26.3231 | 0.04253 | 0.9789 | 0.38981 | 0.00084374 | 34789.0376 | 0.02374 | 1.6918 | 26.3409 | 30.6026 | 2.095 | 0.18894
2025-02-07 02:43 | 0.34438 | 0.39082 | 26.3227 | 0.042573 | 0.9789 | 0.37835 | 0.00081895 | 33766.8654 | 0.02374 | 1.6918 | 25.6739 | 29.8275 | 2.0385 | 0.18384
2025-02-07 02:44 | 0.32585 | 0.36979 | 26.3223 | 0.042446 | 0.9789 | 0.35799 | 0.00077488 | 31949.7404 | 0.023741 | 1.6918 | 24.4812 | 28.4415 | 1.9282 | 0.1739
2025-02-07 02:45 | 0.3189 | 0.3619 | 26.322 | 0.042212 | 0.9789 | 0.35036 | 0.00075835 | 31268.2929 | 0.023741 | 1.6918 | 24.0315 | 27.9188 | 1.8786 | 0.16943
2025-02-07 02:46 | 0.32431 | 0.36804 | 26.3221 | 0.042151 | 0.9789 | 0.3563 | 0.00077121 | 31798.2903 | 0.023741 | 1.6918 | 24.3814 | 28.3254 | 1.9062 | 0.17192
2025-02-07 02:47 | 0.32045 | 0.36365 | 26.3223 | 0.042457 | 0.9789 | 0.35206 | 0.00076203 | 31419.776 | 0.023741 | 1.6918 | 24.1316 | 28.0353 | 1.8983 | 0.1712
2025-02-07 02:48 | 0.30732 | 0.34876 | 26.3225 | 0.042412 | 0.9789 | 0.33763 | 0.00073081 | 30132.7362 | 0.02374 | 1.6918 | 23.279 | 27.0449 | 1.8223 | 0.16435
2025-02-07 02:49 | 0.31774 | 0.36059 | 26.3228 | 0.042155 | 0.9789 | 0.34909 | 0.0007556 | 31154.8623 | 0.02374 | 1.6918 | 23.9565 | 27.8321 | 1.8697 | 0.16862
2025-02-07 02:50 | 0.34168 | 0.38775 | 26.3228 | 0.042212 | 0.9789 | 0.37538 | 0.00081252 | 33501.8972 | 0.02374 | 1.6918 | 25.5006 | 29.6261 | 2.0061 | 0.18093
2025-02-07 02:51 | 0.32778 | 0.37198 | 26.3221 | 0.042421 | 0.9789 | 0.36011 | 0.00077947 | 32138.9906 | 0.023741 | 1.6918 | 24.6059 | 28.5862 | 1.9379 | 0.17478
2025-02-07 02:52 | 0.31968 | 0.36278 | 26.3214 | 0.04215 | 0.9789 | 0.35121 | 0.00076019 | 31343.9041 | 0.023741 | 1.6917 | 24.0816 | 27.9766 | 1.8802 | 0.16957
2025-02-07 02:53 | 0.32933 | 0.37373 | 26.3206 | 0.04225 | 0.97891 | 0.36181 | 0.00078314 | 32290.1441 | 0.023742 | 1.6917 | 24.7056 | 28.701 | 1.9387 | 0.17485
2025-02-07 02:54 | 0.33898 | 0.38468 | 26.3198 | 0.042411 | 0.97891 | 0.37242 | 0.00080609 | 33236.3758 | 0.023742 | 1.6917 | 25.327 | 29.4224 | 2.0002 | 0.18039
2025-02-07 02:55 | 0.3413 | 0.38731 | 26.3191 | 0.042147 | 0.97891 | 0.37496 | 0.0008116 | 33463.3643 | 0.023743 | 1.6916 | 25.4758 | 29.5947 | 2.0007 | 0.18043
2025-02-07 02:56 | 0.34052 | 0.38643 | 26.3183 | 0.041673 | 0.97891 | 0.37411 | 0.00080977 | 33387.5174 | 0.023743 | 1.6916 | 25.4262 | 29.5366 | 1.9738 | 0.17802
2025-02-07 02:57 | 0.31852 | 0.36146 | 26.3177 | 0.041556 | 0.97891 | 0.34993 | 0.00075743 | 31229.7231 | 0.023744 | 1.6916 | 24.0065 | 27.887 | 1.8471 | 0.16659
2025-02-07 02:58 | 0.31427 | 0.35664 | 26.3181 | 0.041565 | 0.97891 | 0.34527 | 0.00074734 | 30813.3801 | 0.023744 | 1.6916 | 23.731 | 27.5671 | 1.8241 | 0.16451
2025-02-07 02:59 | 0.31388 | 0.3562 | 26.3185 | 0.041678 | 0.97891 | 0.34484 | 0.00074642 | 30775.5976 | 0.023743 | 1.6916 | 23.7059 | 27.5383 | 1.8269 | 0.16477
2025-02-07 03:00 | 0.30385 | 0.34481 | 26.3189 | 0.041865 | 0.97891 | 0.33382 | 0.00072255 | 29791.453 | 0.023743 | 1.6916 | 23.0524 | 26.7794 | 1.7792 | 0.16046
2025-02-07 03:01 | 0.29342 | 0.33298 | 26.3193 | 0.041787 | 0.97891 | 0.32236 | 0.00069776 | 28769.4496 | 0.023743 | 1.6916 | 22.3706 | 25.9877 | 1.7179 | 0.15493
2025-02-07 03:02 | 0.29419 | 0.33386 | 26.3197 | 0.041719 | 0.97891 | 0.32321 | 0.00069959 | 28845.2146 | 0.023742 | 1.6917 | 22.4213 | 26.0467 | 1.7194 | 0.15507
2025-02-07 03:03 | 0.3162 | 0.35883 | 26.3197 | 0.041919 | 0.97891 | 0.34739 | 0.00075193 | 31002.9343 | 0.023742 | 1.6917 | 23.8563 | 27.7138 | 1.8505 | 0.16689
2025-02-07 03:04 | 0.32431 | 0.36803 | 26.3197 | 0.042012 | 0.97891 | 0.3563 | 0.00077121 | 31797.8818 | 0.023742 | 1.6917 | 24.3814 | 28.3238 | 1.8998 | 0.17133
2025-02-07 03:05 | 0.31466 | 0.35708 | 26.3197 | 0.041956 | 0.97891 | 0.34569 | 0.00074825 | 30851.5163 | 0.023742 | 1.6917 | 23.7561 | 27.5973 | 1.8435 | 0.16626
2025-02-07 03:06 | 0.30307 | 0.34393 | 26.3197 | 0.041889 | 0.97891 | 0.33297 | 0.00072071 | 29715.8775 | 0.023742 | 1.6917 | 23.0021 | 26.7214 | 1.776 | 0.16017
2025-02-07 03:07 | 0.31736 | 0.36014 | 26.3197 | 0.041953 | 0.97891 | 0.34866 | 0.00075468 | 31116.498 | 0.023742 | 1.6917 | 23.9314 | 27.8011 | 1.8584 | 0.16761
2025-02-07 03:08 | 0.32006 | 0.36321 | 26.3197 | 0.042091 | 0.97891 | 0.35163 | 0.00076111 | 31381.4805 | 0.023742 | 1.6917 | 24.1066 | 28.0046 | 1.8796 | 0.16952
2025-02-07 03:09 | 0.29728 | 0.33736 | 26.3196 | 0.042031 | 0.97891 | 0.32661 | 0.00070694 | 29148.0305 | 0.023743 | 1.6916 | 22.6236 | 26.2816 | 1.7496 | 0.15779
2025-02-07 03:10 | 0.29574 | 0.33561 | 26.3186 | 0.04196 | 0.97891 | 0.32491 | 0.00070327 | 28996.4581 | 0.023743 | 1.6916 | 22.5224 | 26.1635 | 1.7379 | 0.15674
2025-02-07 03:11 | 0.29342 | 0.33298 | 26.3175 | 0.04188 | 0.97891 | 0.32236 | 0.00069776 | 28769.1643 | 0.023744 | 1.6916 | 22.3706 | 25.9865 | 1.7216 | 0.15527
2025-02-07 03:12 | 0.2884 | 0.32728 | 26.3164 | 0.042097 | 0.97891 | 0.31685 | 0.00068582 | 28276.8962 | 0.023745 | 1.6915 | 22.0412 | 25.6032 | 1.7023 | 0.15353
2025-02-07 03:13 | 0.29265 | 0.3321 | 26.3154 | 0.0421 | 0.97892 | 0.32152 | 0.00069592 | 28693.1231 | 0.023746 | 1.6915 | 22.32 | 25.9264 | 1.7262 | 0.15569
2025-02-07 03:14 | 0.29497 | 0.33472 | 26.3144 | 0.041926 | 0.97892 | 0.32406 | 0.00070143 | 28920.0883 | 0.023746 | 1.6914 | 22.4719 | 26.1022 | 1.732 | 0.1562
2025-02-07 03:15 | 0.31157 | 0.35356 | 26.3137 | 0.041985 | 0.97892 | 0.3423 | 0.00074091 | 30547.678 | 0.023747 | 1.6914 | 23.5554 | 27.3603 | 1.8272 | 0.16479
2025-02-07 03:16 | 0.31968 | 0.36276 | 26.313 | 0.042142 | 0.97892 | 0.35121 | 0.00076019 | 31342.4903 | 0.023747 | 1.6914 | 24.0816 | 27.9711 | 1.8794 | 0.1695
2025-02-07 03:17 | 0.3274 | 0.37152 | 26.3124 | 0.041946 | 0.97892 | 0.35969 | 0.00077855 | 32099.4437 | 0.023748 | 1.6913 | 24.581 | 28.5507 | 1.9135 | 0.17258
2025-02-07 03:18 | 0.33628 | 0.3816 | 26.3117 | 0.041842 | 0.97892 | 0.36945 | 0.00079967 | 32969.9501 | 0.023748 | 1.6913 | 25.1533 | 29.2149 | 1.958 | 0.17658
2025-02-07 03:19 | 0.32971 | 0.37415 | 26.311 | 0.041838 | 0.97893 | 0.36224 | 0.00078406 | 32326.3174 | 0.023749 | 1.6913 | 24.7305 | 28.7234 | 1.9214 | 0.17329
2025-02-07 03:20 | 0.32624 | 0.3702 | 26.3098 | 0.041908 | 0.97893 | 0.35842 | 0.0007758 | 31985.4289 | 0.02375 | 1.6912 | 24.5062 | 28.462 | 1.9052 | 0.17183
2025-02-07 03:21 | 0.31736 | 0.36012 | 26.3085 | 0.042001 | 0.97893 | 0.34866 | 0.00075468 | 31114.6029 | 0.02375 | 1.6911 | 23.9314 | 27.7936 | 1.8599 | 0.16774
2025-02-07 03:22 | 0.30693 | 0.34829 | 26.3072 | 0.041803 | 0.97893 | 0.33721 | 0.00072989 | 30092.3815 | 0.023751 | 1.6911 | 23.2538 | 27.0059 | 1.7932 | 0.16172
2025-02-07 03:23 | 0.30925 | 0.35092 | 26.3059 | 0.041685 | 0.97894 | 0.33975 | 0.0007354 | 30319.2829 | 0.023752 | 1.691 | 23.4047 | 27.1802 | 1.8009 | 0.16242
2025-02-07 03:24 | 0.29342 | 0.33295 | 26.305 | 0.041593 | 0.97894 | 0.32236 | 0.00069776 | 28767.2143 | 0.023753 | 1.691 | 22.3706 | 25.9788 | 1.7092 | 0.15415
2025-02-07 03:25 | 0.29033 | 0.32945 | 26.3056 | 0.041489 | 0.97894 | 0.31897 | 0.00069041 | 28464.506 | 0.023752 | 1.691 | 22.168 | 25.7439 | 1.6879 | 0.15223
2025-02-07 03:26 | 0.30307 | 0.34391 | 26.3065 | 0.041522 | 0.97893 | 0.33297 | 0.00072071 | 29713.7513 | 0.023752 | 1.6911 | 23.0021 | 26.713 | 1.7598 | 0.15871
2025-02-07 03:27 | 0.30192 | 0.3426 | 26.3074 | 0.041571 | 0.97893 | 0.3317 | 0.00071796 | 29600.333 | 0.023751 | 1.6911 | 22.9264 | 26.6258 | 1.7555 | 0.15832
2025-02-07 03:28 | 0.29651 | 0.33646 | 26.3082 | 0.041731 | 0.97893 | 0.32576 | 0.0007051 | 29070.5392 | 0.023751 | 1.6911 | 22.573 | 26.2158 | 1.7322 | 0.15623
2025-02-07 03:29 | 0.29072 | 0.32989 | 26.3089 | 0.041513 | 0.97893 | 0.3194 | 0.00069133 | 28502.8651 | 0.02375 | 1.6912 | 22.1933 | 25.7753 | 1.6911 | 0.15252
2025-02-07 03:30 | 0.27682 | 0.31412 | 26.309 | 0.041518 | 0.97893 | 0.30413 | 0.00065828 | 27140.1889 | 0.02375 | 1.6912 | 21.2777 | 24.712 | 1.6143 | 0.14559
2025-02-07 03:31 | 0.28609 | 0.32464 | 26.309 | 0.041634 | 0.97893 | 0.31431 | 0.00068031 | 28048.6471 | 0.02375 | 1.6912 | 21.8888 | 25.4217 | 1.6704 | 0.15065
2025-02-07 03:32 | 0.30655 | 0.34786 | 26.309 | 0.041817 | 0.97893 | 0.33679 | 0.00072897 | 30054.825 | 0.02375 | 1.6912 | 23.2287 | 26.9778 | 1.7917 | 0.16159
2025-02-07 03:33 | 0.30307 | 0.34391 | 26.309 | 0.041847 | 0.97893 | 0.33297 | 0.00072071 | 29714.1535 | 0.02375 | 1.6912 | 23.0021 | 26.7146 | 1.7737 | 0.15996
2025-02-07 03:34 | 0.31736 | 0.36012 | 26.309 | 0.041865 | 0.97893 | 0.34866 | 0.00075468 | 31114.6928 | 0.02375 | 1.6912 | 23.9314 | 27.794 | 1.8539 | 0.1672
2025-02-07 03:35 | 0.32006 | 0.36319 | 26.309 | 0.041693 | 0.97893 | 0.35163 | 0.00076111 | 31379.6598 | 0.02375 | 1.6912 | 24.1066 | 27.9974 | 1.8613 | 0.16786
2025-02-07 03:36 | 0.31466 | 0.35706 | 26.3087 | 0.041823 | 0.97893 | 0.34569 | 0.00074825 | 30849.6782 | 0.02375 | 1.6912 | 23.7561 | 27.5901 | 1.8371 | 0.16568
2025-02-07 03:37 | 0.32006 | 0.36319 | 26.3071 | 0.041756 | 0.97893 | 0.35163 | 0.00076111 | 31379.3433 | 0.023751 | 1.6911 | 24.1066 | 27.9962 | 1.864 | 0.16811
2025-02-07 03:38 | 0.29921 | 0.33953 | 26.3054 | 0.041784 | 0.97894 | 0.32873 | 0.00071153 | 29335.0604 | 0.023753 | 1.691 | 22.7498 | 26.4195 | 1.7493 | 0.15777
2025-02-07 03:39 | 0.30037 | 0.34084 | 26.3037 | 0.041672 | 0.97894 | 0.33 | 0.00071428 | 29448.3412 | 0.023754 | 1.6909 | 22.8255 | 26.5063 | 1.751 | 0.15792
2025-02-07 03:40 | 0.29805 | 0.33821 | 26.302 | 0.041841 | 0.97894 | 0.32745 | 0.00070878 | 29220.9603 | 0.023755 | 1.6909 | 22.6741 | 26.3293 | 1.7451 | 0.15738
2025-02-07 03:41 | 0.31813 | 0.36098 | 26.3006 | 0.041627 | 0.97895 | 0.34951 | 0.00075652 | 31188.9733 | 0.023756 | 1.6908 | 23.9815 | 27.8466 | 1.8472 | 0.16659
2025-02-07 03:42 | 0.35365 | 0.40129 | 26.3004 | 0.04154 | 0.97895 | 0.38853 | 0.00084098 | 34671.213 | 0.023756 | 1.6908 | 26.2669 | 30.5002 | 2.0386 | 0.18385
2025-02-07 03:43 | 0.33898 | 0.38464 | 26.3004 | 0.04152 | 0.97895 | 0.37242 | 0.00080609 | 33232.8868 | 0.023756 | 1.6908 | 25.327 | 29.4089 | 1.9571 | 0.17651
2025-02-07 03:44 | 0.33164 | 0.37632 | 26.3004 | 0.041566 | 0.97895 | 0.36436 | 0.00078865 | 32513.7235 | 0.023756 | 1.6908 | 24.8549 | 28.8607 | 1.9189 | 0.17306
2025-02-07 03:45 | 0.32508 | 0.36887 | 26.3004 | 0.041584 | 0.97895 | 0.35715 | 0.00077304 | 31870.2628 | 0.023756 | 1.6908 | 24.4313 | 28.3688 | 1.8836 | 0.16988
2025-02-07 03:46 | 0.31195 | 0.35397 | 26.3004 | 0.041495 | 0.97895 | 0.34272 | 0.00074183 | 30583.3404 | 0.023756 | 1.6908 | 23.5805 | 27.3808 | 1.8073 | 0.163
2025-02-07 03:47 | 0.305 | 0.34609 | 26.3004 | 0.041439 | 0.97895 | 0.33509 | 0.0007253 | 29902.0277 | 0.023756 | 1.6908 | 23.128 | 26.8554 | 1.7666 | 0.15932
2025-02-07 03:48 | 0.31427 | 0.3566 | 26.3005 | 0.041624 | 0.97895 | 0.34527 | 0.00074734 | 30810.4502 | 0.023756 | 1.6908 | 23.731 | 27.5556 | 1.8257 | 0.16466
2025-02-07 03:49 | 0.30809 | 0.34959 | 26.3007 | 0.041708 | 0.97895 | 0.33848 | 0.00073265 | 30204.8726 | 0.023756 | 1.6908 | 23.3293 | 27.0893 | 1.7952 | 0.1619
2025-02-07 03:50 | 0.27643 | 0.31367 | 26.3009 | 0.041684 | 0.97895 | 0.3037 | 0.00065736 | 27101.1452 | 0.023756 | 1.6908 | 21.2522 | 24.6776 | 1.6182 | 0.14594
2025-02-07 03:51 | 0.2606 | 0.29571 | 26.3011 | 0.041556 | 0.97895 | 0.28631 | 0.00061972 | 25549.2935 | 0.023756 | 1.6908 | 20.2013 | 23.4575 | 1.5251 | 0.13755
2025-02-07 03:52 | 0.26099 | 0.29615 | 26.3013 | 0.041713 | 0.97894 | 0.28673 | 0.00062064 | 25587.1744 | 0.023756 | 1.6908 | 20.2271 | 23.4875 | 1.533 | 0.13826
2025-02-07 03:53 | 0.25211 | 0.28607 | 26.3014 | 0.041905 | 0.97894 | 0.27698 | 0.00059952 | 24716.6127 | 0.023755 | 1.6908 | 19.6338 | 22.7986 | 1.4901 | 0.13439
2025-02-07 03:54 | 0.2664 | 0.30228 | 26.3008 | 0.041622 | 0.97895 | 0.29267 | 0.00063349 | 26117.0127 | 0.023756 | 1.6908 | 20.5868 | 23.9049 | 1.5598 | 0.14068
2025-02-07 03:55 | 0.27682 | 0.31411 | 26.3001 | 0.041549 | 0.97895 | 0.30413 | 0.00065828 | 27138.8886 | 0.023756 | 1.6908 | 21.2777 | 24.7068 | 1.6151 | 0.14566
2025-02-07 03:56 | 0.26292 | 0.29834 | 26.2995 | 0.041093 | 0.97895 | 0.28886 | 0.00062523 | 25776.1772 | 0.023757 | 1.6907 | 20.3557 | 23.6358 | 1.5208 | 0.13716
2025-02-07 03:57 | 0.2664 | 0.30228 | 26.2989 | 0.041056 | 0.97895 | 0.29267 | 0.00063349 | 26116.7399 | 0.023757 | 1.6907 | 20.5868 | 23.9038 | 1.5385 | 0.13876
2025-02-07 03:58 | 0.27296 | 0.30972 | 26.2983 | 0.032966 | 0.97895 | 0.29988 | 0.0006491 | 26760.1079 | 0.023758 | 1.6907 | 21.0223 | 24.4091 | 1.2643 | 0.11403
2025-02-07 03:59 | 0.2691 | 0.30534 | 26.2978 | 0.0148 | 0.97895 | 0.29564 | 0.00063992 | 26381.5419 | 0.023758 | 1.6907 | 20.7663 | 24.1116 | 0.55994 | 0.0505
2025-02-07 04:00 | 0.29805 | 0.3382 | 26.2974 | 0.014121 | 0.97895 | 0.32745 | 0.00070878 | 29220.2342 | 0.023758 | 1.6907 | 22.6741 | 26.3265 | 0.58888 | 0.05311
2025-02-07 04:01 | 0.31968 | 0.36273 | 26.2969 | 0.01416 | 0.97895 | 0.35121 | 0.00076019 | 31339.7642 | 0.023759 | 1.6906 | 24.0816 | 27.9604 | 0.63118 | 0.056925
2025-02-07 04:02 | 0.30616 | 0.3474 | 26.2965 | 0.014201 | 0.97895 | 0.33636 | 0.00072806 | 30014.9453 | 0.023759 | 1.6906 | 23.2035 | 26.9406 | 0.6075 | 0.054789
2025-02-07 04:03 | 0.27952 | 0.31717 | 26.2963 | 0.014057 | 0.97895 | 0.30709 | 0.00066471 | 27403.2707 | 0.023759 | 1.6906 | 21.4563 | 24.9118 | 0.55143 | 0.049732
2025-02-07 04:04 | 0.27064 | 0.30709 | 26.2969 | 0.014194 | 0.97895 | 0.29734 | 0.00064359 | 26532.8068 | 0.023759 | 1.6906 | 20.8687 | 24.23 | 0.53995 | 0.048697
2025-02-07 04:05 | 0.27141 | 0.30797 | 26.2975 | 0.014104 | 0.97895 | 0.29819 | 0.00064543 | 26608.5993 | 0.023758 | 1.6907 | 20.9199 | 24.2898 | 0.53799 | 0.04852
2025-02-07 04:06 | 0.27643 | 0.31367 | 26.2981 | 0.014241 | 0.97895 | 0.3037 | 0.00065736 | 27100.744 | 0.023758 | 1.6907 | 21.2522 | 24.676 | 0.55278 | 0.049854
2025-02-07 04:07 | 0.28917 | 0.32812 | 26.2988 | 0.014261 | 0.97895 | 0.3177 | 0.00068766 | 28349.8991 | 0.023757 | 1.6907 | 22.0919 | 25.6514 | 0.57784 | 0.052114
2025-02-07 04:08 | 0.28995 | 0.329 | 26.2991 | 0.014184 | 0.97895 | 0.31855 | 0.0006895 | 28425.6429 | 0.023757 | 1.6907 | 22.1426 | 25.7104 | 0.57621 | 0.051967
2025-02-07 04:09 | 0.27952 | 0.31717 | 26.2979 | 0.014043 | 0.97895 | 0.30709 | 0.00066471 | 27403.512 | 0.023758 | 1.6907 | 21.4563 | 24.9128 | 0.55091 | 0.049685
2025-02-07 04:10 | 0.2745 | 0.31147 | 26.2966 | 0.013915 | 0.97895 | 0.30158 | 0.00065277 | 26911.2732 | 0.023759 | 1.6906 | 21.1245 | 24.5268 | 0.53653 | 0.048389
2025-02-07 04:11 | 0.28261 | 0.32067 | 26.2953 | 0.014002 | 0.97896 | 0.31049 | 0.00067205 | 27705.9273 | 0.02376 | 1.6906 | 21.66 | 25.1478 | 0.55502 | 0.050056
2025-02-07 04:12 | 0.28647 | 0.32505 | 26.2941 | 0.014285 | 0.97896 | 0.31473 | 0.00068123 | 28084.2287 | 0.023761 | 1.6905 | 21.9142 | 25.4422 | 0.57358 | 0.05173
2025-02-07 04:13 | 0.29188 | 0.33118 | 26.2929 | 0.014231 | 0.97896 | 0.32067 | 0.00069409 | 28613.9465 | 0.023761 | 1.6905 | 22.2693 | 25.8538 | 0.58167 | 0.052459
2025-02-07 04:14 | 0.2745 | 0.31147 | 26.2924 | 0.01426 | 0.97896 | 0.30158 | 0.00065277 | 26910.6638 | 0.023762 | 1.6904 | 21.1245 | 24.5244 | 0.54974 | 0.04958
2025-02-07 04:15 | 0.25597 | 0.29044 | 26.292 | 0.014262 | 0.97896 | 0.28122 | 0.0006087 | 25093.8512 | 0.023762 | 1.6904 | 19.8921 | 23.0934 | 0.51439 | 0.046391
2025-02-07 04:16 | 0.2718 | 0.3084 | 26.2916 | 0.014137 | 0.97896 | 0.29861 | 0.00064634 | 26645.5956 | 0.023762 | 1.6904 | 20.9455 | 24.3161 | 0.5399 | 0.048693
2025-02-07 04:17 | 0.28068 | 0.31847 | 26.2912 | 0.014164 | 0.97897 | 0.30837 | 0.00066746 | 27516.0559 | 0.023763 | 1.6904 | 21.5327 | 24.9975 | 0.55774 | 0.050301
2025-02-07 04:18 | 0.26833 | 0.30445 | 26.2907 | 0.014166 | 0.97897 | 0.29479 | 0.00063808 | 26304.8336 | 0.023763 | 1.6904 | 20.715 | 24.048 | 0.5344 | 0.048196
2025-02-07 04:19 | 0.2664 | 0.30226 | 26.2903 | 0.014057 | 0.97897 | 0.29267 | 0.00063349 | 26115.5253 | 0.023763 | 1.6903 | 20.5868 | 23.8989 | 0.52665 | 0.047497
2025-02-07 04:20 | 0.28068 | 0.31847 | 26.2898 | 0.014085 | 0.97897 | 0.30837 | 0.00066746 | 27515.8544 | 0.023764 | 1.6903 | 21.5327 | 24.9967 | 0.5546 | 0.050018
2025-02-07 04:21 | 0.27412 | 0.31102 | 26.2893 | 0.014055 | 0.97897 | 0.30116 | 0.00065185 | 26872.3636 | 0.023764 | 1.6903 | 21.099 | 24.4929 | 0.54108 | 0.048799
2025-02-07 04:22 | 0.26099 | 0.29613 | 26.2889 | 0.014024 | 0.97897 | 0.28673 | 0.00062064 | 25585.4546 | 0.023764 | 1.6903 | 20.2271 | 23.4805 | 0.51522 | 0.046466
2025-02-07 04:23 | 0.25983 | 0.29481 | 26.2884 | 0.014069 | 0.97897 | 0.28546 | 0.00061788 | 25471.846 | 0.023765 | 1.6903 | 20.1498 | 23.3906 | 0.51466 | 0.046416
2025-02-07 04:24 | 0.27141 | 0.30795 | 26.288 | 0.014087 | 0.97897 | 0.29819 | 0.00064543 | 26607.2262 | 0.023765 | 1.6902 | 20.9199 | 24.2843 | 0.53719 | 0.048448
2025-02-07 04:25 | 0.26485 | 0.30051 | 26.2876 | 0.0141 | 0.97897 | 0.29098 | 0.00062982 | 25963.7562 | 0.023765 | 1.6902 | 20.4841 | 23.7782 | 0.52527 | 0.047373
2025-02-07 04:26 | 0.26138 | 0.29656 | 26.2876 | 0.013963 | 0.97897 | 0.28716 | 0.00062156 | 25623.1186 | 0.023765 | 1.6902 | 20.2528 | 23.5097 | 0.51367 | 0.046327
2025-02-07 04:27 | 0.26794 | 0.30401 | 26.2876 | 0.013974 | 0.97897 | 0.29437 | 0.00063716 | 26266.5355 | 0.023765 | 1.6902 | 20.6894 | 24.0165 | 0.52638 | 0.047473
2025-02-07 04:28 | 0.26948 | 0.30576 | 26.2876 | 0.013976 | 0.97897 | 0.29607 | 0.00064084 | 26417.9278 | 0.023765 | 1.6902 | 20.7919 | 24.1355 | 0.52933 | 0.047739
2025-02-07 04:29 | 0.26601 | 0.30182 | 26.2876 | 0.014037 | 0.97897 | 0.29225 | 0.00063257 | 26077.2955 | 0.023765 | 1.6902 | 20.5611 | 23.8676 | 0.52511 | 0.047358
2025-02-07 04:30 | 0.26871 | 0.30489 | 26.2876 | 0.014038 | 0.97897 | 0.29522 | 0.000639 | 26342.2327 | 0.023765 | 1.6902 | 20.7407 | 24.076 | 0.53025 | 0.047822
2025-02-07 04:31 | 0.25713 | 0.29175 | 26.2876 | 0.014054 | 0.97897 | 0.28249 | 0.00061146 | 25206.791 | 0.023765 | 1.6902 | 19.9695 | 23.1808 | 0.50902 | 0.045908
2025-02-07 04:32 | 0.24864 | 0.28211 | 26.2875 | 0.014006 | 0.97897 | 0.27316 | 0.00059126 | 24374.1277 | 0.023765 | 1.6902 | 19.4008 | 22.5207 | 0.49128 | 0.044308
2025-02-07 04:33 | 0.24593 | 0.27904 | 26.2873 | 0.013836 | 0.97897 | 0.27019 | 0.00058483 | 24109.166 | 0.023765 | 1.6902 | 19.2193 | 22.3099 | 0.48028 | 0.043316
2025-02-07 04:34 | 0.22895 | 0.25977 | 26.2871 | 0.013864 | 0.97897 | 0.25153 | 0.00054443 | 22443.8288 | 0.023766 | 1.6902 | 18.072 | 20.9779 | 0.44951 | 0.040541
2025-02-07 04:35 | 0.23165 | 0.26283 | 26.2869 | 0.014035 | 0.97897 | 0.2545 | 0.00055086 | 22708.7377 | 0.023766 | 1.6902 | 18.2553 | 21.1906 | 0.46017 | 0.041502
2025-02-07 04:36 | 0.22393 | 0.25407 | 26.2867 | 0.0141 | 0.97897 | 0.24601 | 0.0005325 | 21951.754 | 0.023766 | 1.6902 | 17.7307 | 20.5816 | 0.44757 | 0.040365
2025-02-07 04:37 | 0.22084 | 0.25057 | 26.2864 | 0.013992 | 0.97897 | 0.24262 | 0.00052515 | 21648.9399 | 0.023766 | 1.6902 | 17.5202 | 20.3371 | 0.43831 | 0.03953
2025-02-07 04:38 | 0.2413 | 0.27378 | 26.2859 | 0.013914 | 0.97898 | 0.2651 | 0.00057381 | 23654.8165 | 0.023766 | 1.6901 | 18.9076 | 21.9473 | 0.4743 | 0.042776
2025-02-07 04:39 | 0.23937 | 0.27159 | 26.2855 | 0.013942 | 0.97898 | 0.26298 | 0.00056922 | 23465.5193 | 0.023767 | 1.6901 | 18.7774 | 21.796 | 0.47163 | 0.042535
2025-02-07 04:40 | 0.22933 | 0.2602 | 26.285 | 0.013943 | 0.97898 | 0.25195 | 0.00054535 | 22481.4257 | 0.023767 | 1.6901 | 18.0982 | 21.0073 | 0.45276 | 0.040834
2025-02-07 04:41 | 0.22624 | 0.2567 | 26.2846 | 0.01396 | 0.97898 | 0.24856 | 0.00053801 | 22178.5914 | 0.023767 | 1.6901 | 17.8884 | 20.7635 | 0.44747 | 0.040356
2025-02-07 04:42 | 0.19343 | 0.21946 | 26.2841 | 0.013841 | 0.97898 | 0.21251 | 0.00045997 | 18961.5129 | 0.023768 | 1.6901 | 15.6329 | 18.1453 | 0.382 | 0.034452
2025-02-07 04:43 | 0.19111 | 0.21683 | 26.2836 | 0.013551 | 0.97898 | 0.20996 | 0.00045446 | 18734.3822 | 0.023768 | 1.69 | 15.4717 | 17.9581 | 0.36971 | 0.033343
2025-02-07 04:44 | 0.20501 | 0.2326 | 26.2833 | 0.013481 | 0.97898 | 0.22523 | 0.00048751 | 20096.8482 | 0.023768 | 1.69 | 16.4346 | 19.0756 | 0.39332 | 0.035473
2025-02-07 04:45 | 0.21312 | 0.2418 | 26.2835 | 0.013519 | 0.97898 | 0.23414 | 0.00050679 | 20891.6576 | 0.023768 | 1.69 | 16.9921 | 19.7227 | 0.40931 | 0.036915
2025-02-07 04:46 | 0.21505 | 0.24399 | 26.2837 | 0.013518 | 0.97898 | 0.23626 | 0.00051138 | 21080.9179 | 0.023768 | 1.69 | 17.1244 | 19.8763 | 0.41283 | 0.037232
2025-02-07 04:47 | 0.2081 | 0.23611 | 26.2839 | 0.013138 | 0.97898 | 0.22862 | 0.00049486 | 20399.6908 | 0.023768 | 1.6901 | 16.6473 | 19.3228 | 0.38882 | 0.035066
2025-02-07 04:48 | 0.18686 | 0.21202 | 26.2841 | 0.012923 | 0.97898 | 0.2053 | 0.00044436 | 18318.1112 | 0.023768 | 1.6901 | 15.1756 | 17.6146 | 0.3451 | 0.031123
2025-02-07 04:49 | 0.17991 | 0.20413 | 26.2843 | 0.012625 | 0.97898 | 0.19766 | 0.00042784 | 17636.8757 | 0.023768 | 1.6901 | 14.6889 | 17.0498 | 0.32514 | 0.029324
2025-02-07 04:50 | 0.20269 | 0.22998 | 26.2843 | 0.012319 | 0.97898 | 0.22269 | 0.000482 | 19869.8724 | 0.023768 | 1.6901 | 16.2748 | 18.8905 | 0.35554 | 0.032066
2025-02-07 04:51 | 0.22315 | 0.25319 | 26.2843 | 0.012042 | 0.97898 | 0.24517 | 0.00053066 | 21875.783 | 0.023768 | 1.6901 | 17.6781 | 20.5194 | 0.38096 | 0.034358
2025-02-07 04:52 | 0.21003 | 0.2383 | 26.2843 | 0.011887 | 0.97898 | 0.23074 | 0.00049945 | 20588.9722 | 0.023768 | 1.6901 | 16.7801 | 19.477 | 0.35491 | 0.032008
2025-02-07 04:53 | 0.19536 | 0.22165 | 26.2843 | 0.011679 | 0.97898 | 0.21463 | 0.00046456 | 19150.7724 | 0.023768 | 1.6901 | 15.767 | 18.3011 | 0.3254 | 0.029347
2025-02-07 04:54 | 0.19188 | 0.21771 | 26.2843 | 0.011761 | 0.97898 | 0.21081 | 0.0004563 | 18810.1451 | 0.023768 | 1.6901 | 15.5255 | 18.0208 | 0.32213 | 0.029053
2025-02-07 04:55 | 0.19458 | 0.22078 | 26.2843 | 0.011753 | 0.97898 | 0.21378 | 0.00046272 | 19075.0765 | 0.023768 | 1.6901 | 15.7134 | 18.2388 | 0.32623 | 0.029422
2025-02-07 04:56 | 0.19458 | 0.22078 | 26.2845 | 0.01176 | 0.97898 | 0.21378 | 0.00046272 | 19075.0962 | 0.023767 | 1.6901 | 15.7134 | 18.2389 | 0.32643 | 0.02944
2025-02-07 04:57 | 0.19072 | 0.2164 | 26.2853 | 0.011627 | 0.97898 | 0.20954 | 0.00045354 | 18696.7043 | 0.023767 | 1.6901 | 15.4449 | 17.9276 | 0.31661 | 0.028555
2025-02-07 04:58 | 0.18339 | 0.20808 | 26.2862 | 0.011671 | 0.97898 | 0.20148 | 0.0004361 | 17977.6844 | 0.023766 | 1.6902 | 14.9326 | 17.3334 | 0.30613 | 0.027609
2025-02-07 04:59 | 0.18841 | 0.21377 | 26.2871 | 0.011753 | 0.97897 | 0.20699 | 0.00044803 | 18469.7914 | 0.023766 | 1.6902 | 15.2834 | 17.7409 | 0.31635 | 0.028531
2025-02-07 05:00 | 0.19536 | 0.22166 | 26.2879 | 0.011895 | 0.97897 | 0.21463 | 0.00046456 | 19151.1428 | 0.023765 | 1.6902 | 15.767 | 18.3026 | 0.33146 | 0.029894
2025-02-07 05:01 | 0.17837 | 0.20238 | 26.2886 | 0.011883 | 0.97897 | 0.19596 | 0.00042416 | 17485.8886 | 0.023765 | 1.6903 | 14.5804 | 16.9256 | 0.30356 | 0.027377
2025-02-07 05:02 | 0.16022 | 0.18179 | 26.2886 | 0.011808 | 0.97897 | 0.17603 | 0.00038101 | 15707.0256 | 0.023764 | 1.6903 | 13.2954 | 15.4338 | 0.27223 | 0.024552
2025-02-07 05:03 | 0.17103 | 0.19406 | 26.2886 | 0.01195 | 0.97897 | 0.1879 | 0.00040672 | 16766.7766 | 0.023764 | 1.6903 | 14.0633 | 16.3252 | 0.29326 | 0.026449
2025-02-07 05:04 | 0.19574 | 0.2221 | 26.2886 | 0.011894 | 0.97897 | 0.21505 | 0.00046548 | 19189.0647 | 0.023764 | 1.6903 | 15.7938 | 18.334 | 0.33206 | 0.029947
2025-02-07 05:05 | 0.19999 | 0.22691 | 26.2886 | 0.011841 | 0.97897 | 0.21972 | 0.00047558 | 19605.3955 | 0.023764 | 1.6903 | 16.088 | 18.6756 | 0.33743 | 0.030432
2025-02-07 05:06 | 0.19265 | 0.21859 | 26.2886 | 0.011872 | 0.97897 | 0.21166 | 0.00045813 | 18886.278 | 0.023764 | 1.6903 | 15.5792 | 18.085 | 0.32644 | 0.029441
2025-02-07 05:07 | 0.20733 | 0.23524 | 26.2886 | 0.012028 | 0.97897 | 0.22778 | 0.00049302 | 20324.5121 | 0.023764 | 1.6903 | 16.5942 | 19.2632 | 0.35476 | 0.031995
2025-02-07 05:08 | 0.21427 | 0.24312 | 26.2885 | 0.012045 | 0.97897 | 0.23541 | 0.00050955 | 21005.7691 | 0.023765 | 1.6903 | 17.0715 | 19.8172 | 0.36663 | 0.033065
2025-02-07 05:09 | 0.19574 | 0.2221 | 26.2881 | 0.012171 | 0.97897 | 0.21505 | 0.00046548 | 19189.0089 | 0.023765 | 1.6902 | 15.7938 | 18.3338 | 0.33981 | 0.030647
2025-02-07 05:10 | 0.20771 | 0.23567 | 26.2876 | 0.012033 | 0.97897 | 0.2282 | 0.00049394 | 20362.2507 | 0.023765 | 1.6902 | 16.6208 | 19.2936 | 0.35554 | 0.032065
2025-02-07 05:11 | 0.20346 | 0.23085 | 26.2872 | 0.012166 | 0.97897 | 0.22353 | 0.00048384 | 19945.8719 | 0.023766 | 1.6902 | 16.3281 | 18.9537 | 0.35242 | 0.031784
2025-02-07 05:12 | 0.19381 | 0.2199 | 26.2867 | 0.012502 | 0.97897 | 0.21293 | 0.00046089 | 18999.6262 | 0.023766 | 1.6902 | 15.6597 | 18.1776 | 0.34572 | 0.03118
2025-02-07 05:13 | 0.19536 | 0.22165 | 26.2862 | 0.012453 | 0.97898 | 0.21463 | 0.00046456 | 19150.9701 | 0.023766 | 1.6902 | 15.767 | 18.3019 | 0.347 | 0.031295
2025-02-07 05:14 | 0.19188 | 0.21771 | 26.2858 | 0.012739 | 0.97898 | 0.21081 | 0.0004563 | 18810.2924 | 0.023767 | 1.6901 | 15.5255 | 18.0214 | 0.34893 | 0.031469
2025-02-07 05:15 | 0.19652 | 0.22297 | 26.2852 | 0.013038 | 0.97898 | 0.2159 | 0.00046731 | 19264.4072 | 0.023767 | 1.6901 | 15.8473 | 18.3947 | 0.36533 | 0.032948
2025-02-07 05:16 | 0.19536 | 0.22165 | 26.2844 | 0.012932 | 0.97898 | 0.21463 | 0.00046456 | 19150.7782 | 0.023767 | 1.6901 | 15.767 | 18.3011 | 0.36031 | 0.032496
2025-02-07 05:17 | 0.18416 | 0.20895 | 26.2835 | 0.013024 | 0.97898 | 0.20233 | 0.00043793 | 18053.1196 | 0.023768 | 1.69 | 14.9866 | 17.395 | 0.34298 | 0.030933
2025-02-07 05:18 | 0.16833 | 0.19099 | 26.2827 | 0.013066 | 0.97898 | 0.18494 | 0.00040029 | 16501.3078 | 0.023769 | 1.69 | 13.8719 | 16.1008 | 0.31574 | 0.028476
2025-02-07 05:19 | 0.17296 | 0.19624 | 26.2818 | 0.013055 | 0.97898 | 0.19003 | 0.00041131 | 16955.3934 | 0.023769 | 1.69 | 14.1997 | 16.4809 | 0.32377 | 0.0292
2025-02-07 05:20 | 0.18107 | 0.20544 | 26.2812 | 0.013066 | 0.97899 | 0.19893 | 0.00043059 | 17750.1139 | 0.02377 | 1.6899 | 14.7702 | 17.1428 | 0.33855 | 0.030533
2025-02-07 05:21 | 0.14864 | 0.16865 | 26.2811 | 0.012984 | 0.97899 | 0.1633 | 0.00035347 | 14570.986 | 0.02377 | 1.6899 | 12.4645 | 14.4667 | 0.27852 | 0.025119
2025-02-07 05:22 | 0.13744 | 0.15594 | 26.2811 | 0.012841 | 0.97899 | 0.151 | 0.00032684 | 13473.4313 | 0.02377 | 1.6899 | 11.6527 | 13.5245 | 0.25556 | 0.023049
2025-02-07 05:23 | 0.14246 | 0.16164 | 26.2811 | 0.012681 | 0.97899 | 0.15652 | 0.00033878 | 13965.4389 | 0.02377 | 1.6899 | 12.0177 | 13.9482 | 0.26118 | 0.023555
2025-02-07 05:24 | 0.14401 | 0.16339 | 26.2811 | 0.012597 | 0.97899 | 0.15821 | 0.00034245 | 14116.8259 | 0.02377 | 1.6899 | 12.1297 | 14.0781 | 0.26216 | 0.023644
2025-02-07 05:25 | 0.16717 | 0.18967 | 26.2811 | 0.01278 | 0.97899 | 0.18366 | 0.00039754 | 16387.6289 | 0.02377 | 1.6899 | 13.7898 | 16.0049 | 0.30678 | 0.027668
2025-02-07 05:26 | 0.16717 | 0.18967 | 26.2811 | 0.013004 | 0.97899 | 0.18366 | 0.00039754 | 16387.6289 | 0.02377 | 1.6899 | 13.7898 | 16.0049 | 0.31217 | 0.028154
2025-02-07 05:27 | 0.16177 | 0.18354 | 26.281 | 0.013072 | 0.97899 | 0.17772 | 0.00038468 | 15857.7662 | 0.02377 | 1.6899 | 13.4055 | 15.5588 | 0.30408 | 0.027425
2025-02-07 05:28 | 0.18069 | 0.205 | 26.2806 | 0.013006 | 0.97899 | 0.19851 | 0.00042967 | 17712.2153 | 0.02377 | 1.6899 | 14.7431 | 17.1112 | 0.3363 | 0.03033
2025-02-07 05:29 | 0.18069 | 0.205 | 26.2802 | 0.012676 | 0.97899 | 0.19851 | 0.00042967 | 17712.1741 | 0.02377 | 1.6899 | 14.7431 | 17.111 | 0.32776 | 0.02956
2025-02-07 05:30 | 0.17489 | 0.19843 | 26.2797 | 0.012468 | 0.97899 | 0.19215 | 0.0004159 | 17144.4359 | 0.023771 | 1.6899 | 14.3358 | 16.6381 | 0.31248 | 0.028182
2025-02-07 05:31 | 0.17644 | 0.20018 | 26.2793 | 0.012429 | 0.97899 | 0.19384 | 0.00041957 | 17295.7809 | 0.023771 | 1.6898 | 14.4446 | 16.7642 | 0.31414 | 0.028331
2025-02-07 05:32 | 0.17451 | 0.19799 | 26.2791 | 0.012352 | 0.97899 | 0.19172 | 0.00041498 | 17106.5337 | 0.023771 | 1.6898 | 14.3086 | 16.6063 | 0.30892 | 0.027861
2025-02-07 05:33 | 0.15675 | 0.17784 | 26.2797 | 0.012322 | 0.97899 | 0.17221 | 0.00037275 | 15365.653 | 0.023771 | 1.6899 | 13.047 | 15.1423 | 0.2781 | 0.025081
2025-02-07 05:34 | 0.15443 | 0.17522 | 26.2804 | 0.012396 | 0.97899 | 0.16967 | 0.00036724 | 15138.627 | 0.02377 | 1.6899 | 12.881 | 14.9499 | 0.27582 | 0.024875
2025-02-07 05:35 | 0.14941 | 0.16952 | 26.281 | 0.012363 | 0.97899 | 0.16415 | 0.00035531 | 14646.6727 | 0.02377 | 1.6899 | 12.5202 | 14.5313 | 0.26653 | 0.024037
2025-02-07 05:36 | 0.15945 | 0.18091 | 26.2817 | 0.012059 | 0.97898 | 0.17518 | 0.00037918 | 15630.7416 | 0.023769 | 1.6899 | 13.2402 | 15.3673 | 0.27667 | 0.024952
2025-02-07 05:37 | 0.16795 | 0.19055 | 26.2822 | 0.011867 | 0.97898 | 0.18451 | 0.00039937 | 16463.4149 | 0.023769 | 1.69 | 13.8446 | 16.0689 | 0.28613 | 0.025806
2025-02-07 05:38 | 0.17219 | 0.19537 | 26.2822 | 0.011695 | 0.97898 | 0.18918 | 0.00040947 | 16879.7335 | 0.023769 | 1.69 | 14.1451 | 16.4177 | 0.2888 | 0.026046
2025-02-07 05:39 | 0.15134 | 0.17171 | 26.2822 | 0.011607 | 0.97898 | 0.16627 | 0.0003599 | 14835.9989 | 0.023769 | 1.69 | 12.6592 | 14.693 | 0.25333 | 0.022848
2025-02-07 05:40 | 0.12972 | 0.14718 | 26.2822 | 0.011495 | 0.97898 | 0.14252 | 0.00030848 | 12716.5705 | 0.023769 | 1.69 | 11.0874 | 12.8688 | 0.21644 | 0.01952
2025-02-07 05:41 | 0.13551 | 0.15375 | 26.2822 | 0.011118 | 0.97898 | 0.14888 | 0.00032225 | 13284.2745 | 0.023769 | 1.69 | 11.5118 | 13.3613 | 0.21829 | 0.019687
2025-02-07 05:42 | 0.14362 | 0.16295 | 26.2822 | 0.010725 | 0.97898 | 0.15779 | 0.00034153 | 14079.06 | 0.023769 | 1.69 | 12.1017 | 14.046 | 0.22262 | 0.020078
2025-02-07 05:43 | 0.14362 | 0.16295 | 26.2822 | 0.010458 | 0.97898 | 0.15779 | 0.00034153 | 14079.06 | 0.023769 | 1.69 | 12.1017 | 14.046 | 0.21708 | 0.019578
2025-02-07 05:44 | 0.14748 | 0.16733 | 26.282 | 0.01004 | 0.97898 | 0.16203 | 0.00035072 | 14457.5172 | 0.023769 | 1.69 | 12.3809 | 14.37 | 0.21378 | 0.01928
2025-02-07 05:45 | 0.15868 | 0.18004 | 26.2814 | 0.0095454 | 0.97899 | 0.17433 | 0.00037734 | 15555.0255 | 0.02377 | 1.6899 | 13.1851 | 15.3032 | 0.21799 | 0.01966
2025-02-07 05:46 | 0.17644 | 0.20018 | 26.2808 | 0.0090953 | 0.97899 | 0.19384 | 0.00041957 | 17295.9168 | 0.02377 | 1.6899 | 14.4446 | 16.7648 | 0.22989 | 0.020733
2025-02-07 05:47 | 0.17451 | 0.19799 | 26.2801 | 0.0087234 | 0.97899 | 0.19172 | 0.00041498 | 17106.6239 | 0.023771 | 1.6899 | 14.3086 | 16.6067 | 0.21818 | 0.019677
2025-02-07 05:48 | 0.14324 | 0.16251 | 26.2795 | 0.0084245 | 0.97899 | 0.15736 | 0.00034062 | 14041.0074 | 0.023771 | 1.6899 | 12.0737 | 14.0126 | 0.17441 | 0.01573
2025-02-07 05:49 | 0.14131 | 0.16032 | 26.2792 | 0.0083273 | 0.97899 | 0.15524 | 0.00033603 | 13851.7562 | 0.023771 | 1.6898 | 11.9336 | 13.8499 | 0.17017 | 0.015347
2025-02-07 05:50 | 0.15945 | 0.18091 | 26.28 | 0.0080616 | 0.97899 | 0.17518 | 0.00037918 | 15630.6014 | 0.023771 | 1.6899 | 13.2402 | 15.3667 | 0.18495 | 0.01668
2025-02-07 05:51 | 0.16022 | 0.18179 | 26.2809 | 0.0075342 | 0.97899 | 0.17603 | 0.00038101 | 15706.3671 | 0.02377 | 1.6899 | 13.2954 | 15.431 | 0.17366 | 0.015662
2025-02-07 05:52 | 0.15945 | 0.18091 | 26.2817 | 0.0069712 | 0.97898 | 0.17518 | 0.00037918 | 15630.7464 | 0.023769 | 1.69 | 13.2402 | 15.3673 | 0.15994 | 0.014425
2025-02-07 05:53 | 0.16022 | 0.18179 | 26.2826 | 0.0064284 | 0.97898 | 0.17603 | 0.00038101 | 15706.5129 | 0.023769 | 1.69 | 13.2954 | 15.4316 | 0.14818 | 0.013364
2025-02-07 05:54 | 0.14401 | 0.16339 | 26.283 | 0.0060371 | 0.97898 | 0.15821 | 0.00034245 | 14116.9703 | 0.023768 | 1.69 | 12.1297 | 14.0787 | 0.12565 | 0.011332
2025-02-07 05:55 | 0.13474 | 0.15288 | 26.2822 | 0.0056647 | 0.97898 | 0.14803 | 0.00032042 | 13208.5831 | 0.023769 | 1.69 | 11.4554 | 13.2958 | 0.11061 | 0.0099759
2025-02-07 05:56 | 0.15212 | 0.17259 | 26.2814 | 0.005255 | 0.97899 | 0.16712 | 0.00036173 | 14911.6265 | 0.02377 | 1.6899 | 12.7147 | 14.7572 | 0.11525 | 0.010394
2025-02-07 05:57 | 0.16524 | 0.18748 | 26.2805 | 0.004835 | 0.97899 | 0.18154 | 0.00039295 | 16198.3412 | 0.02377 | 1.6899 | 13.6528 | 15.8456 | 0.11478 | 0.010352
2025-02-07 05:58 | 0.17605 | 0.19974 | 26.2796 | 0.0043008 | 0.97899 | 0.19342 | 0.00041865 | 17257.9654 | 0.023771 | 1.6899 | 14.4175 | 16.7328 | 0.10847 | 0.0097829
2025-02-07 05:59 | 0.17219 | 0.19536 | 26.2789 | 0.0037389 | 0.97899 | 0.18918 | 0.00040947 | 16879.4378 | 0.023771 | 1.6898 | 14.1451 | 16.4165 | 0.092321 | 0.0083262
2025-02-07 06:00 | 0.15713 | 0.17828 | 26.2787 | 0.003204 | 0.97899 | 0.17263 | 0.00037367 | 15403.4131 | 0.023772 | 1.6898 | 13.0746 | 15.174 | 0.072482 | 0.006537
2025-02-07 06:01 | 0.1359 | 0.15419 | 26.2785 | 0.0026613 | 0.97899 | 0.14931 | 0.00032317 | 13321.8556 | 0.023772 | 1.6898 | 11.54 | 13.3929 | 0.05239 | 0.0047249
2025-02-07 06:02 | 0.13088 | 0.14849 | 26.2783 | 0.0024237 | 0.97899 | 0.14379 | 0.00031124 | 12829.8406 | 0.023772 | 1.6898 | 11.1725 | 12.9663 | 0.046022 | 0.0041506
2025-02-07 06:03 | 0.14864 | 0.16864 | 26.2781 | 0.0025085 | 0.97899 | 0.1633 | 0.00035347 | 14570.7459 | 0.023772 | 1.6898 | 12.4645 | 14.4657 | 0.053806 | 0.0048527
2025-02-07 06:04 | 0.14864 | 0.16864 | 26.278 | 0.0027304 | 0.97899 | 0.1633 | 0.00035347 | 14570.7419 | 0.023772 | 1.6898 | 12.4645 | 14.4657 | 0.058566 | 0.0052819
2025-02-07 06:05 | 0.13938 | 0.15813 | 26.2784 | 0.0030471 | 0.97899 | 0.15312 | 0.00033144 | 13662.4658 | 0.023772 | 1.6898 | 11.7933 | 13.6868 | 0.061451 | 0.0055422
2025-02-07 06:06 | 0.14324 | 0.16251 | 26.2788 | 0.0033133 | 0.97899 | 0.15736 | 0.00034062 | 14040.9601 | 0.023771 | 1.6898 | 12.0737 | 14.0124 | 0.068594 | 0.0061863
2025-02-07 06:07 | 0.122 | 0.13842 | 26.2793 | 0.0036709 | 0.97899 | 0.13404 | 0.00029012 | 11959.4442 | 0.023771 | 1.6898 | 10.5174 | 12.2064 | 0.065164 | 0.005877
2025-02-07 06:08 | 0.12277 | 0.1393 | 26.2797 | 0.0042153 | 0.97899 | 0.13488 | 0.00029196 | 12035.1651 | 0.023771 | 1.6899 | 10.5747 | 12.2729 | 0.075283 | 0.0067896
2025-02-07 06:09 | 0.14671 | 0.16645 | 26.2799 | 0.0046683 | 0.97899 | 0.16118 | 0.00034888 | 14381.6594 | 0.023771 | 1.6899 | 12.3252 | 14.3046 | 0.098894 | 0.008919
2025-02-07 06:10 | 0.13822 | 0.15682 | 26.2795 | 0.0050538 | 0.97899 | 0.15185 | 0.00032868 | 13549.0079 | 0.023771 | 1.6899 | 11.709 | 13.5893 | 0.10111 | 0.0091192
2025-02-07 06:11 | 0.11698 | 0.13272 | 26.2791 | 0.0055982 | 0.97899 | 0.12852 | 0.00027819 | 11467.4298 | 0.023771 | 1.6898 | 10.1442 | 11.7732 | 0.09545 | 0.0086084
2025-02-07 06:12 | 0.11737 | 0.13316 | 26.2787 | 0.0061903 | 0.97899 | 0.12895 | 0.0002791 | 11505.2491 | 0.023772 | 1.6898 | 10.173 | 11.8065 | 0.10588 | 0.0095489
2025-02-07 06:13 | 0.10463 | 0.11871 | 26.2782 | 0.0067704 | 0.97899 | 0.11495 | 0.00024881 | 10256.3002 | 0.023772 | 1.6898 | 9.2158 | 10.6954 | 0.10371 | 0.009353
2025-02-07 06:14 | 0.090343 | 0.1025 | 26.277 | 0.0072751 | 0.97899 | 0.099254 | 0.00021484 | 8855.9348 | 0.023773 | 1.6897 | 8.1228 | 9.4266 | 0.096771 | 0.0087275
2025-02-07 06:15 | 0.091501 | 0.10381 | 26.2737 | 0.0077122 | 0.979 | 0.10053 | 0.00021759 | 8969.3108 | 0.023775 | 1.6896 | 8.2123 | 9.5297 | 0.10384 | 0.009365
2025-02-07 06:16 | 0.12548 | 0.14235 | 26.2702 | 0.0080937 | 0.97901 | 0.13785 | 0.00029838 | 12299.4596 | 0.023778 | 1.6894 | 10.7745 | 12.5021 | 0.14756 | 0.013308
2025-02-07 06:17 | 0.12741 | 0.14454 | 26.2668 | 0.0084553 | 0.97901 | 0.13997 | 0.00030297 | 12488.4505 | 0.02378 | 1.6893 | 10.9169 | 12.6663 | 0.15641 | 0.014106
2025-02-07 06:18 | 0.10926 | 0.12395 | 26.2634 | 0.0087692 | 0.97902 | 0.12004 | 0.00025982 | 10709.5938 | 0.023782 | 1.6891 | 9.5657 | 11.0976 | 0.13997 | 0.012623
2025-02-07 06:19 | 0.098837 | 0.11213 | 26.261 | 0.0090354 | 0.97903 | 0.10859 | 0.00023503 | 9687.7073 | 0.023784 | 1.689 | 8.7754 | 10.1801 | 0.13097 | 0.011812
2025-02-07 06:20 | 0.080305 | 0.091103 | 26.2615 | 0.009254 | 0.97903 | 0.088226 | 0.00019097 | 7871.2838 | 0.023784 | 1.689 | 7.3403 | 8.5154 | 0.10986 | 0.0099077
2025-02-07 06:21 | 0.065634 | 0.074459 | 26.2622 | 0.0094646 | 0.97902 | 0.072108 | 0.00015608 | 6433.2832 | 0.023783 | 1.6891 | 6.1711 | 7.1592 | 0.092514 | 0.0083437
2025-02-07 06:22 | 0.056368 | 0.063948 | 26.2628 | 0.0096434 | 0.97902 | 0.061928 | 0.00013404 | 5525.0742 | 0.023783 | 1.6891 | 5.414 | 6.281 | 0.081393 | 0.0073406
2025-02-07 06:23 | 0.052893 | 0.060006 | 26.2635 | 0.0097984 | 0.97902 | 0.05811 | 0.00012578 | 5184.5056 | 0.023782 | 1.6891 | 5.1258 | 5.9466 | 0.077775 | 0.0070143
2025-02-07 06:24 | 0.055596 | 0.063072 | 26.2632 | 0.0099577 | 0.97902 | 0.06108 | 0.00013221 | 5449.3994 | 0.023783 | 1.6891 | 5.3502 | 6.207 | 0.082935 | 0.0074797
2025-02-07 06:25 | 0.049804 | 0.056501 | 26.2605 | 0.010047 | 0.97903 | 0.054717 | 0.00011844 | 4881.6827 | 0.023784 | 1.689 | 4.8673 | 5.6464 | 0.07524 | 0.0067857
2025-02-07 06:26 | 0.039766 | 0.045112 | 26.2577 | 0.010149 | 0.97903 | 0.043689 | 9.4565e-05 | 3897.7186 | 0.023786 | 1.6889 | 4.0107 | 4.6524 | 0.061129 | 0.0055131
2025-02-07 06:27 | 0.031273 | 0.035476 | 26.2549 | 0.010197 | 0.97904 | 0.034357 | 7.4366e-05 | 3065.1499 | 0.023788 | 1.6888 | 3.2619 | 3.7836 | 0.048657 | 0.0043883
2025-02-07 06:28 | 0.025095 | 0.028468 | 26.2521 | 0.010224 | 0.97904 | 0.027571 | 5.9677e-05 | 2459.6511 | 0.02379 | 1.6886 | 2.6995 | 3.131 | 0.0394 | 0.0035534
2025-02-07 06:29 | 0.045171 | 0.051242 | 26.2492 | 0.010224 | 0.97905 | 0.049627 | 0.00010742 | 4427.3022 | 0.023792 | 1.6885 | 4.4753 | 5.1902 | 0.069642 | 0.0062809
2025-02-07 06:30 | 0.079147 | 0.089781 | 26.246 | 0.010224 | 0.97906 | 0.086953 | 0.00018821 | 7757.1043 | 0.023795 | 1.6884 | 7.2491 | 8.4066 | 0.11963 | 0.010789
2025-02-07 06:31 | 0.086868 | 0.098539 | 26.2428 | 0.010244 | 0.97906 | 0.095437 | 0.00020657 | 8513.7471 | 0.023797 | 1.6882 | 7.8534 | 9.1066 | 0.13109 | 0.011823
2025-02-07 06:32 | 0.082621 | 0.09372 | 26.2395 | 0.010292 | 0.97907 | 0.090771 | 0.00019647 | 8097.3787 | 0.023799 | 1.6881 | 7.522 | 8.7217 | 0.12549 | 0.011317
2025-02-07 06:33 | 0.095748 | 0.10861 | 26.2363 | 0.010319 | 0.97908 | 0.10519 | 0.00022769 | 9383.7148 | 0.023802 | 1.6879 | 8.539 | 9.9001 | 0.14497 | 0.013074
2025-02-07 06:34 | 0.12586 | 0.14276 | 26.2341 | 0.010298 | 0.97908 | 0.13828 | 0.0002993 | 12334.8935 | 0.023803 | 1.6878 | 10.803 | 12.5244 | 0.1881 | 0.016965
2025-02-07 06:35 | 0.12972 | 0.14714 | 26.2342 | 0.010292 | 0.97908 | 0.14252 | 0.00030848 | 12713.2726 | 0.023803 | 1.6878 | 11.0874 | 12.8541 | 0.19351 | 0.017452
2025-02-07 06:36 | 0.10501 | 0.11912 | 26.2344 | 0.010319 | 0.97908 | 0.11537 | 0.00024972 | 10291.7088 | 0.023803 | 1.6878 | 9.245 | 10.7182 | 0.15841 | 0.014287
2025-02-07 06:37 | 0.11969 | 0.13576 | 26.2346 | 0.010319 | 0.97908 | 0.13149 | 0.00028461 | 11729.535 | 0.023803 | 1.6878 | 10.3455 | 11.9941 | 0.1796 | 0.016198
2025-02-07 06:38 | 0.12509 | 0.14189 | 26.2348 | 0.010319 | 0.97908 | 0.13743 | 0.00029747 | 12259.2703 | 0.023803 | 1.6879 | 10.746 | 12.4585 | 0.18738 | 0.016899
2025-02-07 06:39 | 0.13474 | 0.15284 | 26.2348 | 0.010319 | 0.97908 | 0.14803 | 0.00032042 | 13205.1999 | 0.023803 | 1.6879 | 11.4554 | 13.2809 | 0.20121 | 0.018147
2025-02-07 06:40 | 0.14053 | 0.15941 | 26.2342 | 0.010298 | 0.97908 | 0.1544 | 0.00033419 | 13772.7124 | 0.023803 | 1.6878 | 11.8775 | 13.7701 | 0.20907 | 0.018856
2025-02-07 06:41 | 0.12779 | 0.14495 | 26.2335 | 0.010251 | 0.97908 | 0.1404 | 0.00030389 | 12524.0437 | 0.023804 | 1.6878 | 10.9454 | 12.6892 | 0.18998 | 0.017134
2025-02-07 06:42 | 0.12509 | 0.14189 | 26.2329 | 0.010224 | 0.97908 | 0.13743 | 0.00029747 | 12259.1424 | 0.023804 | 1.6878 | 10.746 | 12.4579 | 0.18563 | 0.016742
2025-02-07 06:43 | 0.12509 | 0.14189 | 26.2322 | 0.010202 | 0.97908 | 0.13743 | 0.00029747 | 12259.0998 | 0.023805 | 1.6877 | 10.746 | 12.4577 | 0.18524 | 0.016706
2025-02-07 06:44 | 0.12509 | 0.14189 | 26.2316 | 0.010197 | 0.97909 | 0.13743 | 0.00029747 | 12259.0572 | 0.023805 | 1.6877 | 10.746 | 12.4576 | 0.18515 | 0.016698
2025-02-07 06:45 | 0.13281 | 0.15065 | 26.231 | 0.010202 | 0.97909 | 0.14591 | 0.00031583 | 13015.7434 | 0.023805 | 1.6877 | 11.3141 | 13.1159 | 0.19618 | 0.017693
2025-02-07 06:46 | 0.14748 | 0.16729 | 26.2303 | 0.010176 | 0.97909 | 0.16203 | 0.00035072 | 14453.4784 | 0.023806 | 1.6877 | 12.3809 | 14.3524 | 0.21634 | 0.019511
2025-02-07 06:47 | 0.1471 | 0.16685 | 26.2297 | 0.010154 | 0.97909 | 0.16161 | 0.0003498 | 14415.592 | 0.023806 | 1.6876 | 12.3531 | 14.3199 | 0.21534 | 0.019421
2025-02-07 06:48 | 0.14864 | 0.1686 | 26.229 | 0.01015 | 0.97909 | 0.1633 | 0.00035347 | 14566.8861 | 0.023807 | 1.6876 | 12.4645 | 14.4489 | 0.21739 | 0.019606
2025-02-07 06:49 | 0.16408 | 0.18611 | 26.2277 | 0.010154 | 0.97909 | 0.18027 | 0.00039019 | 16080.2183 | 0.023808 | 1.6875 | 13.5704 | 15.7304 | 0.23907 | 0.021561
2025-02-07 06:50 | 0.17065 | 0.19356 | 26.225 | 0.010085 | 0.9791 | 0.18748 | 0.0004058 | 16723.1798 | 0.02381 | 1.6874 | 14.036 | 16.2689 | 0.2465 | 0.022231
2025-02-07 06:51 | 0.16833 | 0.19093 | 26.2222 | 0.010033 | 0.9791 | 0.18494 | 0.00040029 | 16495.9203 | 0.023812 | 1.6873 | 13.8719 | 16.0778 | 0.24201 | 0.021827
2025-02-07 06:52 | 0.15366 | 0.17428 | 26.2194 | 0.0099899 | 0.97911 | 0.16882 | 0.0003654 | 15057.976 | 0.023814 | 1.6872 | 12.8256 | 14.8641 | 0.22082 | 0.019915
2025-02-07 06:53 | 0.15405 | 0.17472 | 26.2166 | 0.0099804 | 0.97912 | 0.16924 | 0.00036632 | 15095.5826 | 0.023816 | 1.687 | 12.8533 | 14.8952 | 0.22112 | 0.019943
2025-02-07 06:54 | 0.18339 | 0.208 | 26.215 | 0.0099899 | 0.97912 | 0.20148 | 0.0004361 | 17970.776 | 0.023817 | 1.687 | 14.9326 | 17.3041 | 0.2615 | 0.023584
2025-02-07 06:55 | 0.18802 | 0.21325 | 26.2162 | 0.0099375 | 0.97912 | 0.20657 | 0.00044712 | 18424.8923 | 0.023816 | 1.687 | 15.2565 | 17.6799 | 0.26641 | 0.024027
2025-02-07 06:56 | 0.16254 | 0.18435 | 26.2175 | 0.009916 | 0.97911 | 0.17857 | 0.00038652 | 15927.9951 | 0.023815 | 1.6871 | 13.4605 | 15.5992 | 0.23128 | 0.020859
2025-02-07 06:57 | 0.17026 | 0.19311 | 26.2188 | 0.0098898 | 0.97911 | 0.18706 | 0.00040488 | 16684.7855 | 0.023814 | 1.6871 | 14.0086 | 16.2349 | 0.24115 | 0.021749
2025-02-07 06:58 | 0.16215 | 0.18392 | 26.2201 | 0.0099112 | 0.97911 | 0.17815 | 0.0003856 | 15890.3825 | 0.023813 | 1.6872 | 13.433 | 15.5682 | 0.23066 | 0.020803
2025-02-07 06:59 | 0.17567 | 0.19924 | 26.2206 | 0.0099375 | 0.97911 | 0.19299 | 0.00041774 | 17214.6304 | 0.023813 | 1.6872 | 14.3903 | 16.6779 | 0.24968 | 0.022518
2025-02-07 07:00 | 0.19652 | 0.22289 | 26.2194 | 0.0099375 | 0.97911 | 0.2159 | 0.00046731 | 19257.5581 | 0.023814 | 1.6872 | 15.8473 | 18.366 | 0.27792 | 0.025065
2025-02-07 07:01 | 0.20115 | 0.22814 | 26.2181 | 0.0099375 | 0.97911 | 0.22099 | 0.00047833 | 19711.4307 | 0.023815 | 1.6871 | 16.1681 | 18.7372 | 0.28417 | 0.025629
2025-02-07 07:02 | 0.19806 | 0.22464 | 26.2168 | 0.0099811 | 0.97912 | 0.2176 | 0.00047099 | 19408.6241 | 0.023815 | 1.687 | 15.9544 | 18.489 | 0.28122 | 0.025362
2025-02-07 07:03 | 0.18609 | 0.21106 | 26.2155 | 0.0099883 | 0.97912 | 0.20445 | 0.00044253 | 18235.6559 | 0.023816 | 1.687 | 15.1217 | 17.5234 | 0.26514 | 0.023912
2025-02-07 07:04 | 0.19034 | 0.21588 | 26.2144 | 0.009982 | 0.97912 | 0.20911 | 0.00045262 | 18651.7127 | 0.023817 | 1.6869 | 15.418 | 17.8663 | 0.27074 | 0.024417
2025-02-07 07:05 | 0.19999 | 0.22682 | 26.2138 | 0.010077 | 0.97912 | 0.21972 | 0.00047558 | 19597.4698 | 0.023818 | 1.6869 | 16.088 | 18.6425 | 0.28655 | 0.025843
2025-02-07 07:06 | 0.19072 | 0.21631 | 26.2131 | 0.01015 | 0.97912 | 0.20954 | 0.00045354 | 18689.4136 | 0.023818 | 1.6869 | 15.4449 | 17.8969 | 0.27583 | 0.024877
2025-02-07 07:07 | 0.19883 | 0.22551 | 26.2125 | 0.010087 | 0.97912 | 0.21844 | 0.00047282 | 19483.8353 | 0.023819 | 1.6869 | 16.0078 | 18.549 | 0.28522 | 0.025723
2025-02-07 07:08 | 0.21003 | 0.23821 | 26.2118 | 0.010007 | 0.97913 | 0.23074 | 0.00049945 | 20580.9121 | 0.023819 | 1.6868 | 16.7801 | 19.4435 | 0.29817 | 0.026891
2025-02-07 07:09 | 0.21273 | 0.24127 | 26.2112 | 0.010011 | 0.97913 | 0.23371 | 0.00050587 | 20845.6682 | 0.023819 | 1.6868 | 16.9656 | 19.6582 | 0.30192 | 0.027229
2025-02-07 07:10 | 0.22393 | 0.25397 | 26.2105 | 0.010074 | 0.97913 | 0.24601 | 0.0005325 | 21942.7317 | 0.02382 | 1.6868 | 17.7307 | 20.5445 | 0.31908 | 0.028777
2025-02-07 07:11 | 0.20733 | 0.23514 | 26.2099 | 0.010131 | 0.97913 | 0.22778 | 0.00049302 | 20315.8726 | 0.02382 | 1.6867 | 16.5942 | 19.2273 | 0.29813 | 0.026888
2025-02-07 07:12 | 0.20501 | 0.23251 | 26.2093 | 0.010125 | 0.97913 | 0.22523 | 0.00048751 | 20088.81 | 0.023821 | 1.6867 | 16.4346 | 19.0421 | 0.29476 | 0.026584
2025-02-07 07:13 | 0.21505 | 0.24389 | 26.2086 | 0.010198 | 0.97913 | 0.23626 | 0.00051138 | 21072.3687 | 0.023821 | 1.6867 | 17.1244 | 19.841 | 0.31075 | 0.028026
2025-02-07 07:14 | 0.21582 | 0.24477 | 26.2078 | 0.010224 | 0.97913 | 0.23711 | 0.00051322 | 21147.9444 | 0.023822 | 1.6866 | 17.1772 | 19.9018 | 0.31259 | 0.028191
2025-02-07 07:15 | 0.21312 | 0.2417 | 26.2068 | 0.010179 | 0.97914 | 0.23414 | 0.00050679 | 20883.0038 | 0.023823 | 1.6866 | 16.9921 | 19.6868 | 0.30749 | 0.027732
2025-02-07 07:16 | 0.20926 | 0.23732 | 26.2057 | 0.01015 | 0.97914 | 0.2299 | 0.00049761 | 20504.5713 | 0.023823 | 1.6866 | 16.727 | 19.3792 | 0.30131 | 0.027175
2025-02-07 07:17 | 0.20771 | 0.23557 | 26.2047 | 0.010199 | 0.97914 | 0.2282 | 0.00049394 | 20353.1295 | 0.023824 | 1.6865 | 16.6208 | 19.2557 | 0.3006 | 0.02711
2025-02-07 07:18 | 0.2247 | 0.25483 | 26.2036 | 0.010224 | 0.97914 | 0.24686 | 0.00053434 | 22017.5709 | 0.023825 | 1.6865 | 17.7833 | 20.602 | 0.32481 | 0.029294
2025-02-07 07:19 | 0.25057 | 0.28417 | 26.2027 | 0.010184 | 0.97914 | 0.27528 | 0.00059585 | 24552.12 | 0.023826 | 1.6864 | 19.5303 | 22.6254 | 0.35897 | 0.032375
2025-02-07 07:20 | 0.25057 | 0.28417 | 26.2022 | 0.010148 | 0.97914 | 0.27528 | 0.00059585 | 24552.0568 | 0.023826 | 1.6864 | 19.5303 | 22.6252 | 0.35771 | 0.032261
2025-02-07 07:21 | 0.21814 | 0.24739 | 26.2018 | 0.010136 | 0.97915 | 0.23965 | 0.00051873 | 21374.2345 | 0.023826 | 1.6864 | 17.3357 | 20.0825 | 0.31303 | 0.028232
2025-02-07 07:22 | 0.20501 | 0.2325 | 26.2013 | 0.01012 | 0.97915 | 0.22523 | 0.00048751 | 20087.9475 | 0.023826 | 1.6864 | 16.4346 | 19.0385 | 0.29455 | 0.026565
2025-02-07 07:23 | 0.21312 | 0.24169 | 26.2008 | 0.010116 | 0.97915 | 0.23414 | 0.00050679 | 20882.3335 | 0.023827 | 1.6863 | 16.9921 | 19.6841 | 0.30554 | 0.027556
2025-02-07 07:24 | 0.21312 | 0.24169 | 26.2004 | 0.010013 | 0.97915 | 0.23414 | 0.00050679 | 20882.2817 | 0.023827 | 1.6863 | 16.9921 | 19.6839 | 0.30242 | 0.027275
2025-02-07 07:25 | 0.21505 | 0.24388 | 26.1999 | 0.010066 | 0.97915 | 0.23626 | 0.00051138 | 21071.3803 | 0.023827 | 1.6863 | 17.1244 | 19.8369 | 0.30664 | 0.027656
2025-02-07 07:26 | 0.21968 | 0.24914 | 26.1995 | 0.010197 | 0.97915 | 0.24135 | 0.0005224 | 21525.2888 | 0.023828 | 1.6863 | 17.4412 | 20.2036 | 0.317 | 0.02859
2025-02-07 07:27 | 0.22624 | 0.25658 | 26.199 | 0.010224 | 0.97915 | 0.24856 | 0.00053801 | 22168.3449 | 0.023828 | 1.6863 | 17.8884 | 20.7215 | 0.3269 | 0.029482
2025-02-07 07:28 | 0.23937 | 0.27146 | 26.1985 | 0.010141 | 0.97915 | 0.26298 | 0.00056922 | 23454.5042 | 0.023828 | 1.6862 | 18.7774 | 21.7511 | 0.34217 | 0.03086
2025-02-07 07:29 | 0.24246 | 0.27497 | 26.1981 | 0.0099915 | 0.97915 | 0.26637 | 0.00057657 | 23757.084 | 0.023829 | 1.6862 | 18.9856 | 21.992 | 0.34127 | 0.030779
2025-02-07 07:30 | 0.22393 | 0.25395 | 26.1976 | 0.0099788 | 0.97915 | 0.24601 | 0.0005325 | 21941.2009 | 0.023829 | 1.6862 | 17.7307 | 20.5382 | 0.31594 | 0.028494
2025-02-07 07:31 | 0.21312 | 0.24169 | 26.1972 | 0.010095 | 0.97915 | 0.23414 | 0.00050679 | 20881.9184 | 0.023829 | 1.6862 | 16.9921 | 19.6823 | 0.30486 | 0.027495
2025-02-07 07:32 | 0.20926 | 0.23731 | 26.1967 | 0.010238 | 0.97916 | 0.2299 | 0.00049761 | 20503.5721 | 0.02383 | 1.6861 | 16.727 | 19.3751 | 0.30383 | 0.027402
2025-02-07 07:33 | 0.21736 | 0.2465 | 26.1964 | 0.010278 | 0.97916 | 0.2388 | 0.00051689 | 21297.9529 | 0.02383 | 1.6861 | 17.2829 | 20.0188 | 0.31628 | 0.028524
2025-02-07 07:34 | 0.22277 | 0.25263 | 26.1964 | 0.010141 | 0.97916 | 0.24474 | 0.00052975 | 21827.5628 | 0.02383 | 1.6861 | 17.6518 | 20.4462 | 0.31947 | 0.028813
2025-02-07 07:35 | 0.21543 | 0.24431 | 26.1964 | 0.0099295 | 0.97916 | 0.23668 | 0.0005123 | 21108.8046 | 0.02383 | 1.6861 | 17.1508 | 19.8658 | 0.30297 | 0.027325
2025-02-07 07:36 | 0.22972 | 0.26051 | 26.1964 | 0.0098564 | 0.97916 | 0.25238 | 0.00054627 | 22508.4923 | 0.02383 | 1.6861 | 18.1244 | 20.9935 | 0.31975 | 0.028837
2025-02-07 07:37 | 0.23281 | 0.26402 | 26.1964 | 0.0099581 | 0.97916 | 0.25577 | 0.00055362 | 22811.1272 | 0.02383 | 1.6861 | 18.3338 | 21.2361 | 0.32719 | 0.029509
2025-02-07 07:38 | 0.24091 | 0.27321 | 26.1964 | 0.010047 | 0.97916 | 0.26468 | 0.0005729 | 23605.5438 | 0.02383 | 1.6861 | 18.8815 | 21.8705 | 0.34107 | 0.03076
2025-02-07 07:39 | 0.23705 | 0.26883 | 26.1964 | 0.010046 | 0.97916 | 0.26044 | 0.00056371 | 23227.2501 | 0.02383 | 1.6861 | 18.621 | 21.5688 | 0.3358 | 0.030285
2025-02-07 07:40 | 0.22393 | 0.25395 | 26.1965 | 0.0099168 | 0.97916 | 0.24601 | 0.0005325 | 21941.0661 | 0.02383 | 1.6861 | 17.7307 | 20.5376 | 0.31396 | 0.028316
2025-02-07 07:41 | 0.2054 | 0.23293 | 26.1969 | 0.0097847 | 0.97916 | 0.22565 | 0.00048843 | 20125.3019 | 0.02383 | 1.6862 | 16.4612 | 19.0674 | 0.28526 | 0.025727
2025-02-07 07:42 | 0.19652 | 0.22286 | 26.1974 | 0.0095441 | 0.97915 | 0.2159 | 0.00046731 | 19255.2714 | 0.023829 | 1.6862 | 15.8473 | 18.3565 | 0.26675 | 0.024058
2025-02-07 07:43 | 0.20115 | 0.22812 | 26.1979 | 0.0093056 | 0.97915 | 0.22099 | 0.00047833 | 19709.2765 | 0.023829 | 1.6862 | 16.1681 | 18.7282 | 0.26594 | 0.023985
2025-02-07 07:44 | 0.19806 | 0.22461 | 26.1983 | 0.0090243 | 0.97915 | 0.2176 | 0.00047099 | 19406.6865 | 0.023829 | 1.6862 | 15.9544 | 18.4809 | 0.25412 | 0.022919
2025-02-07 07:45 | 0.18995 | 0.21542 | 26.1988 | 0.0085618 | 0.97915 | 0.20869 | 0.00045171 | 18612.3066 | 0.023828 | 1.6862 | 15.3911 | 17.8285 | 0.23166 | 0.020893
2025-02-07 07:46 | 0.20733 | 0.23512 | 26.1992 | 0.0079633 | 0.97915 | 0.22778 | 0.00049302 | 20314.7024 | 0.023828 | 1.6863 | 16.5942 | 19.2224 | 0.23426 | 0.021128
2025-02-07 07:47 | 0.22393 | 0.25395 | 26.1995 | 0.0074984 | 0.97915 | 0.24601 | 0.0005325 | 21941.4231 | 0.023828 | 1.6863 | 17.7307 | 20.5391 | 0.23742 | 0.021412
2025-02-07 07:48 | 0.21698 | 0.24607 | 26.1993 | 0.0069715 | 0.97915 | 0.23838 | 0.00051597 | 21260.46 | 0.023828 | 1.6863 | 17.2565 | 19.9896 | 0.21419 | 0.019317
2025-02-07 07:49 | 0.21852 | 0.24782 | 26.1991 | 0.0063158 | 0.97915 | 0.24008 | 0.00051965 | 21411.7555 | 0.023828 | 1.6863 | 17.362 | 20.1118 | 0.19536 | 0.017619
2025-02-07 07:50 | 0.20346 | 0.23074 | 26.1989 | 0.0055767 | 0.97915 | 0.22353 | 0.00048384 | 19936.3634 | 0.023828 | 1.6862 | 16.3281 | 18.914 | 0.16113 | 0.014532
2025-02-07 07:51 | 0.18995 | 0.21542 | 26.1987 | 0.0047255 | 0.97915 | 0.20869 | 0.00045171 | 18612.2949 | 0.023828 | 1.6862 | 15.3911 | 17.8285 | 0.12786 | 0.011532
2025-02-07 07:52 | 0.17837 | 0.20228 | 26.1989 | 0.0040794 | 0.97915 | 0.19596 | 0.00042416 | 17477.4201 | 0.023828 | 1.6862 | 14.5804 | 16.8896 | 0.10394 | 0.0093739
2025-02-07 07:53 | 0.16795 | 0.19046 | 26.2001 | 0.0033952 | 0.97915 | 0.18451 | 0.00039937 | 16456.1236 | 0.023827 | 1.6863 | 13.8446 | 16.0376 | 0.081666 | 0.0073652
2025-02-07 07:54 | 0.16833 | 0.1909 | 26.2014 | 0.0027609 | 0.97915 | 0.18494 | 0.00040029 | 16494.0685 | 0.023826 | 1.6864 | 13.8719 | 16.0698 | 0.066559 | 0.0060028
2025-02-07 07:55 | 0.15945 | 0.18083 | 26.2027 | 0.0021554 | 0.97914 | 0.17518 | 0.00037918 | 15624.0773 | 0.023826 | 1.6864 | 13.2402 | 15.3385 | 0.049336 | 0.0044495
2025-02-07 07:56 | 0.14671 | 0.16639 | 26.204 | 0.0014568 | 0.97914 | 0.16118 | 0.00034888 | 14375.7641 | 0.023825 | 1.6865 | 12.3252 | 14.2789 | 0.030792 | 0.002777
2025-02-07 07:57 | 0.12123 | 0.13749 | 26.205 | 0.00079396 | 0.97914 | 0.13319 | 0.00028828 | 11878.9834 | 0.023824 | 1.6865 | 10.4602 | 12.1185 | 0.013978 | 0.0012606
2025-02-07 07:58 | 0.11969 | 0.13574 | 26.2052 | 0.00012161 | 0.97914 | 0.13149 | 0.00028461 | 11727.674 | 0.023824 | 1.6865 | 10.3455 | 11.9857 | 0.0021149 | 0.00019074
2025-02-07 07:59 | 0.11158 | 0.12654 | 26.2054 | -0.0005412 | 0.97914 | 0.12258 | 0.00026533 | 10933.2313 | 0.023824 | 1.6865 | 9.7398 | 11.2841 | -0.0087988 | -0.00079355
2025-02-07 08:00 | 0.086868 | 0.098519 | 26.2056 | 7.393e-05 | 0.97914 | 0.095437 | 0.00020657 | 8512.0412 | 0.023823 | 1.6865 | 7.8534 | 9.0986 | 0.00094498 | 8.5226e-05
2025-02-07 08:01 | 0.061387 | 0.06962 | 26.2059 | 0.0001282 | 0.97914 | 0.067442 | 0.00014598 | 6015.1828 | 0.023823 | 1.6866 | 5.8261 | 6.7499 | 0.0011729 | 0.00010578
2025-02-07 08:02 | 0.052507 | 0.059549 | 26.2062 | -0.0016467 | 0.97914 | 0.057686 | 0.00012486 | 5145.0714 | 0.023823 | 1.6866 | 5.0936 | 5.9013 | -0.012956 | -0.0011685
2025-02-07 08:03 | 0.076058 | 0.086259 | 26.2068 | -0.0021235 | 0.97914 | 0.08356 | 0.00018087 | 7452.8129 | 0.023823 | 1.6866 | 7.0052 | 8.1161 | -0.023885 | -0.0021542
2025-02-07 08:04 | 0.082621 | 0.093703 | 26.2075 | -0.0024637 | 0.97913 | 0.090771 | 0.00019647 | 8095.9771 | 0.023822 | 1.6866 | 7.522 | 8.7151 | -0.03001 | -0.0027066
2025-02-07 08:05 | 0.099609 | 0.11297 | 26.2081 | -0.0032838 | 0.97913 | 0.10943 | 0.00023687 | 9760.6045 | 0.023822 | 1.6867 | 8.8343 | 10.2356 | -0.047881 | -0.0043183
2025-02-07 08:06 | 0.11196 | 0.12698 | 26.2088 | -0.0037543 | 0.97913 | 0.12301 | 0.00026625 | 10971.2603 | 0.023821 | 1.6867 | 9.7688 | 11.3186 | -0.061247 | -0.0055237
2025-02-07 08:07 | 0.122 | 0.13837 | 26.2094 | -0.0034078 | 0.97913 | 0.13404 | 0.00029012 | 11954.932 | 0.023821 | 1.6867 | 10.5174 | 12.1861 | -0.060369 | -0.0054446
2025-02-07 08:08 | 0.1359 | 0.15413 | 26.2101 | -0.0033506 | 0.97913 | 0.14931 | 0.00032317 | 13316.9327 | 0.02382 | 1.6867 | 11.54 | 13.3711 | -0.065825 | -0.0059366
2025-02-07 08:09 | 0.14053 | 0.15939 | 26.2107 | -0.0035604 | 0.97913 | 0.1544 | 0.00033419 | 13770.9671 | 0.02382 | 1.6868 | 11.8775 | 13.7625 | -0.072232 | -0.0065144
2025-02-07 08:10 | 0.16795 | 0.19048 | 26.2113 | -0.0034651 | 0.97913 | 0.18451 | 0.00039937 | 16457.1193 | 0.023819 | 1.6868 | 13.8446 | 16.0419 | -0.083375 | -0.0075193
2025-02-07 08:11 | 0.18377 | 0.20843 | 26.212 | -0.0031249 | 0.97913 | 0.2019 | 0.00043702 | 18008.3123 | 0.023819 | 1.6868 | 14.9596 | 17.3342 | -0.081955 | -0.0073913
2025-02-07 08:12 | 0.20038 | 0.22726 | 26.2122 | -0.0027275 | 0.97912 | 0.22014 | 0.0004765 | 19635.1401 | 0.023819 | 1.6868 | 16.1147 | 18.6728 | -0.077697 | -0.0070073
2025-02-07 08:13 | 0.21427 | 0.24302 | 26.2116 | -0.002451 | 0.97913 | 0.23541 | 0.00050955 | 20997.0464 | 0.023819 | 1.6868 | 17.0715 | 19.7811 | -0.074435 | -0.0067131
2025-02-07 08:14 | 0.21659 | 0.24565 | 26.211 | -0.0019773 | 0.97913 | 0.23796 | 0.00051506 | 21223.9679 | 0.02382 | 1.6868 | 17.2301 | 19.9646 | -0.060668 | -0.0054715
2025-02-07 08:15 | 0.21041 | 0.23864 | 26.2103 | -0.001475 | 0.97913 | 0.23117 | 0.00050037 | 20618.5774 | 0.02382 | 1.6868 | 16.8066 | 19.4736 | -0.044023 | -0.0039703
2025-02-07 08:16 | 0.21891 | 0.24827 | 26.2097 | -0.00099818 | 0.97913 | 0.2405 | 0.00052056 | 21450.8126 | 0.023821 | 1.6867 | 17.3884 | 20.1474 | -0.030938 | -0.0027902
2025-02-07 08:17 | 0.23667 | 0.26842 | 26.2094 | -0.00043232 | 0.97913 | 0.26001 | 0.0005628 | 23191.0593 | 0.023821 | 1.6867 | 18.5949 | 21.5453 | -0.014435 | -0.0013018
2025-02-07 08:18 | 0.25597 | 0.29031 | 26.2101 | 0.00010175 | 0.97913 | 0.28122 | 0.0006087 | 25082.7455 | 0.02382 | 1.6867 | 19.8921 | 23.0486 | 0.0036613 | 0.0003302
2025-02-07 08:19 | 0.26022 | 0.29513 | 26.2107 | 0.00066124 | 0.97913 | 0.28589 | 0.0006188 | 25498.9879 | 0.02382 | 1.6868 | 20.1756 | 23.3774 | 0.024169 | 0.0021798
2025-02-07 08:20 | 0.27412 | 0.31089 | 26.2113 | 0.0014019 | 0.97913 | 0.30116 | 0.00065185 | 26861.0454 | 0.023819 | 1.6868 | 21.099 | 24.4477 | 0.053848 | 0.0048565
2025-02-07 08:21 | 0.305 | 0.34592 | 26.212 | 0.0022813 | 0.97913 | 0.33509 | 0.0007253 | 29887.7456 | 0.023819 | 1.6868 | 23.128 | 26.7992 | 0.097003 | 0.0087484
2025-02-07 08:22 | 0.30848 | 0.34987 | 26.2128 | 0.0031782 | 0.97912 | 0.33891 | 0.00073356 | 30228.3651 | 0.023818 | 1.6869 | 23.3544 | 27.062 | 0.13661 | 0.01232
2025-02-07 08:23 | 0.29612 | 0.33586 | 26.2138 | 0.0042622 | 0.97912 | 0.32533 | 0.00070418 | 29017.8846 | 0.023818 | 1.6869 | 22.5477 | 26.1279 | 0.17622 | 0.015893
2025-02-07 08:24 | 0.28647 | 0.32491 | 26.2149 | 0.0052795 | 0.97912 | 0.31473 | 0.00068123 | 28072.2241 | 0.023817 | 1.687 | 21.9142 | 25.3945 | 0.2115 | 0.019075
2025-02-07 08:25 | 0.28223 | 0.3201 | 26.216 | 0.0061267 | 0.97912 | 0.31006 | 0.00067113 | 27656.2206 | 0.023816 | 1.687 | 21.6345 | 25.071 | 0.24198 | 0.021824
2025-02-07 08:26 | 0.26678 | 0.30258 | 26.2171 | 0.0072266 | 0.97911 | 0.2931 | 0.00063441 | 26143.0355 | 0.023815 | 1.6871 | 20.6125 | 23.8872 | 0.27054 | 0.024399
2025-02-07 08:27 | 0.26215 | 0.29733 | 26.2179 | 0.008251 | 0.97911 | 0.28801 | 0.00062339 | 25689.1423 | 0.023815 | 1.6871 | 20.3042 | 23.5305 | 0.30378 | 0.027397
2025-02-07 08:28 | 0.26138 | 0.29645 | 26.2181 | 0.0090696 | 0.97911 | 0.28716 | 0.00062156 | 25613.5068 | 0.023815 | 1.6871 | 20.2528 | 23.471 | 0.33298 | 0.030031
2025-02-07 08:29 | 0.26987 | 0.30609 | 26.2183 | 0.0096418 | 0.97911 | 0.29649 | 0.00064175 | 26445.8819 | 0.023814 | 1.6871 | 20.8175 | 24.1256 | 0.36495 | 0.032914
2025-02-07 08:30 | 0.27798 | 0.31528 | 26.2185 | 0.010352 | 0.97911 | 0.3054 | 0.00066103 | 27240.4254 | 0.023814 | 1.6871 | 21.3543 | 24.7477 | 0.40305 | 0.03635
2025-02-07 08:31 | 0.27412 | 0.3109 | 26.2187 | 0.011141 | 0.97911 | 0.30116 | 0.00065185 | 26862.1176 | 0.023814 | 1.6871 | 21.099 | 24.452 | 0.42804 | 0.038604
2025-02-07 08:32 | 0.26871 | 0.30477 | 26.2185 | 0.011765 | 0.97911 | 0.29522 | 0.000639 | 26332.4146 | 0.023814 | 1.6871 | 20.7407 | 24.0366 | 0.44348 | 0.039996
2025-02-07 08:33 | 0.27257 | 0.30915 | 26.2175 | 0.012197 | 0.97911 | 0.29946 | 0.00064818 | 26710.6024 | 0.023815 | 1.6871 | 20.9967 | 24.3327 | 0.46605 | 0.042032
2025-02-07 08:34 | 0.27412 | 0.3109 | 26.2164 | 0.012623 | 0.97912 | 0.30116 | 0.00065185 | 26861.7816 | 0.023816 | 1.687 | 21.099 | 24.4506 | 0.48492 | 0.043733
2025-02-07 08:35 | 0.27064 | 0.30696 | 26.2153 | 0.013101 | 0.97912 | 0.29734 | 0.00064359 | 26521.1269 | 0.023817 | 1.687 | 20.8687 | 24.1832 | 0.4972 | 0.044841
2025-02-07 08:36 | 0.27141 | 0.30783 | 26.2143 | 0.013554 | 0.97912 | 0.29819 | 0.00064543 | 26596.6394 | 0.023817 | 1.6869 | 20.9199 | 24.2419 | 0.51574 | 0.046514
2025-02-07 08:37 | 0.2745 | 0.31133 | 26.2141 | 0.01403 | 0.97912 | 0.30158 | 0.00065277 | 26899.2775 | 0.023817 | 1.6869 | 21.1245 | 24.4789 | 0.53967 | 0.048672
2025-02-07 08:38 | 0.28647 | 0.32491 | 26.2158 | 0.014392 | 0.97912 | 0.31473 | 0.00068123 | 28072.3536 | 0.023816 | 1.687 | 21.9142 | 25.395 | 0.57658 | 0.052
2025-02-07 08:39 | 0.29574 | 0.33542 | 26.2175 | 0.014773 | 0.97911 | 0.32491 | 0.00070327 | 28980.6241 | 0.023815 | 1.6871 | 22.5224 | 26.1009 | 0.61008 | 0.055022
2025-02-07 08:40 | 0.29149 | 0.33061 | 26.2192 | 0.01504 | 0.97911 | 0.32024 | 0.00069317 | 28564.7183 | 0.023814 | 1.6872 | 22.244 | 25.7793 | 0.61263 | 0.055252
2025-02-07 08:41 | 0.27412 | 0.31091 | 26.2209 | 0.015087 | 0.97911 | 0.30116 | 0.00065185 | 26862.4356 | 0.023813 | 1.6872 | 21.099 | 24.4532 | 0.57967 | 0.052279
2025-02-07 08:42 | 0.2745 | 0.31135 | 26.2219 | 0.015254 | 0.97911 | 0.30158 | 0.00065277 | 26900.4055 | 0.023812 | 1.6873 | 21.1245 | 24.4834 | 0.58688 | 0.052929
2025-02-07 08:43 | 0.29419 | 0.33368 | 26.2213 | 0.015564 | 0.97911 | 0.32321 | 0.00069959 | 28829.8755 | 0.023812 | 1.6872 | 22.4213 | 25.986 | 0.63963 | 0.057687
2025-02-07 08:44 | 0.29883 | 0.33893 | 26.2206 | 0.01585 | 0.97911 | 0.3283 | 0.00071061 | 29283.7874 | 0.023813 | 1.6872 | 22.7246 | 26.3371 | 0.66114 | 0.059627
2025-02-07 08:45 | 0.28261 | 0.32054 | 26.22 | 0.01585 | 0.97911 | 0.31049 | 0.00067205 | 27694.6486 | 0.023813 | 1.6872 | 21.66 | 25.1029 | 0.62692 | 0.056541
2025-02-07 08:46 | 0.2691 | 0.30521 | 26.2193 | 0.01597 | 0.97911 | 0.29564 | 0.00063992 | 26370.3596 | 0.023814 | 1.6872 | 20.7663 | 24.0668 | 0.60282 | 0.054367
2025-02-07 08:47 | 0.26176 | 0.29689 | 26.2187 | 0.016184 | 0.97911 | 0.28758 | 0.00062247 | 25651.4231 | 0.023814 | 1.6871 | 20.2785 | 23.5011 | 0.59503 | 0.053665
2025-02-07 08:48 | 0.28184 | 0.31966 | 26.218 | 0.016184 | 0.97911 | 0.30964 | 0.00067021 | 27618.6923 | 0.023815 | 1.6871 | 21.6091 | 25.0427 | 0.63842 | 0.057578
2025-02-07 08:49 | 0.28917 | 0.32798 | 26.2174 | 0.016256 | 0.97911 | 0.3177 | 0.00068766 | 28337.4368 | 0.023815 | 1.6871 | 22.0919 | 25.6019 | 0.65712 | 0.059264
2025-02-07 08:50 | 0.29574 | 0.33542 | 26.2168 | 0.016184 | 0.97912 | 0.32491 | 0.00070327 | 28980.5095 | 0.023816 | 1.687 | 22.5224 | 26.1004 | 0.66834 | 0.060276
2025-02-07 08:51 | 0.30114 | 0.34155 | 26.2161 | 0.016065 | 0.97912 | 0.33085 | 0.00071612 | 29510.0764 | 0.023816 | 1.687 | 22.876 | 26.5098 | 0.67495 | 0.060872
2025-02-07 08:52 | 0.28956 | 0.32842 | 26.2166 | 0.016184 | 0.97912 | 0.31812 | 0.00068858 | 28375.1503 | 0.023816 | 1.687 | 22.1173 | 25.6308 | 0.65504 | 0.059077
2025-02-07 08:53 | 0.26755 | 0.30346 | 26.2193 | 0.016399 | 0.97911 | 0.29395 | 0.00063625 | 26219.0255 | 0.023814 | 1.6872 | 20.6638 | 23.9479 | 0.61564 | 0.055523
2025-02-07 08:54 | 0.27296 | 0.3096 | 26.2221 | 0.016566 | 0.9791 | 0.29988 | 0.0006491 | 26749.1056 | 0.023812 | 1.6873 | 21.0223 | 24.365 | 0.63392 | 0.057172
2025-02-07 08:55 | 0.29188 | 0.33106 | 26.2249 | 0.016685 | 0.9791 | 0.32067 | 0.00069409 | 28603.4355 | 0.02381 | 1.6874 | 22.2693 | 25.8121 | 0.68062 | 0.061383
2025-02-07 08:56 | 0.28802 | 0.32668 | 26.2277 | 0.016926 | 0.97909 | 0.31643 | 0.0006849 | 28225.5077 | 0.023808 | 1.6875 | 22.0158 | 25.5199 | 0.68181 | 0.061491
2025-02-07 08:57 | 0.27489 | 0.3118 | 26.2297 | 0.017139 | 0.97909 | 0.302 | 0.00065369 | 26939.3809 | 0.023806 | 1.6876 | 21.1501 | 24.5176 | 0.66044 | 0.059564
2025-02-07 08:58 | 0.2718 | 0.3083 | 26.2302 | 0.017235 | 0.97909 | 0.29861 | 0.00064634 | 26636.7587 | 0.023806 | 1.6876 | 20.9455 | 24.2807 | 0.65702 | 0.059255
2025-02-07 08:59 | 0.28261 | 0.32056 | 26.2306 | 0.017379 | 0.97909 | 0.31049 | 0.00067205 | 27696.2399 | 0.023806 | 1.6877 | 21.66 | 25.1092 | 0.68762 | 0.062014
2025-02-07 09:00 | 0.28261 | 0.32056 | 26.231 | 0.017546 | 0.97909 | 0.31049 | 0.00067205 | 27696.3043 | 0.023805 | 1.6877 | 21.66 | 25.1095 | 0.6942 | 0.062608
2025-02-07 09:01 | 0.28454 | 0.32275 | 26.2315 | 0.017541 | 0.97909 | 0.31261 | 0.00067664 | 27885.5514 | 0.023805 | 1.6877 | 21.7872 | 25.2572 | 0.69853 | 0.062999
2025-02-07 09:02 | 0.28531 | 0.32363 | 26.232 | 0.017595 | 0.97908 | 0.31346 | 0.00067848 | 27961.3006 | 0.023805 | 1.6877 | 21.838 | 25.3164 | 0.7025 | 0.063357
2025-02-07 09:03 | 0.28647 | 0.32494 | 26.2326 | 0.017759 | 0.97908 | 0.31473 | 0.00068123 | 28074.9086 | 0.023804 | 1.6878 | 21.9142 | 25.4052 | 0.71183 | 0.064198
2025-02-07 09:04 | 0.29381 | 0.33326 | 26.2333 | 0.017756 | 0.97908 | 0.32279 | 0.00069868 | 28793.9086 | 0.023804 | 1.6878 | 22.396 | 25.964 | 0.72906 | 0.065752
2025-02-07 09:05 | 0.28493 | 0.32319 | 26.2339 | 0.017759 | 0.97908 | 0.31303 | 0.00067756 | 27923.7561 | 0.023803 | 1.6878 | 21.8126 | 25.2881 | 0.7082 | 0.063871
2025-02-07 09:06 | 0.28029 | 0.31794 | 26.2346 | 0.017805 | 0.97908 | 0.30794 | 0.00066654 | 27469.8068 | 0.023803 | 1.6878 | 21.5072 | 24.9345 | 0.69905 | 0.063046
2025-02-07 09:07 | 0.30616 | 0.34728 | 26.235 | 0.017781 | 0.97908 | 0.33636 | 0.00072806 | 30004.9791 | 0.023803 | 1.6879 | 23.2035 | 26.9014 | 0.7593 | 0.06848
2025-02-07 09:08 | 0.31195 | 0.35385 | 26.2353 | 0.017758 | 0.97908 | 0.34272 | 0.00074183 | 30572.5747 | 0.023802 | 1.6879 | 23.5805 | 27.3386 | 0.77197 | 0.069622
2025-02-07 09:09 | 0.31466 | 0.35692 | 26.2355 | 0.017708 | 0.97908 | 0.34569 | 0.00074825 | 30837.4712 | 0.023802 | 1.6879 | 23.7561 | 27.5423 | 0.77617 | 0.070001
2025-02-07 09:10 | 0.32392 | 0.36743 | 26.2357 | 0.017712 | 0.97908 | 0.35587 | 0.00077029 | 31745.6048 | 0.023802 | 1.6879 | 24.3565 | 28.2385 | 0.79805 | 0.071975
2025-02-07 09:11 | 0.3162 | 0.35867 | 26.2359 | 0.017782 | 0.97908 | 0.34739 | 0.00075193 | 30988.8924 | 0.023802 | 1.6879 | 23.8563 | 27.6587 | 0.78306 | 0.070623
2025-02-07 09:12 | 0.3301 | 0.37443 | 26.2359 | 0.017855 | 0.97908 | 0.36266 | 0.00078498 | 32351.0408 | 0.023802 | 1.6879 | 24.7554 | 28.7011 | 0.81909 | 0.073872
2025-02-07 09:13 | 0.33049 | 0.37487 | 26.2355 | 0.018049 | 0.97908 | 0.36308 | 0.0007859 | 32388.8051 | 0.023802 | 1.6879 | 24.7803 | 28.7297 | 0.8289 | 0.074756
2025-02-07 09:14 | 0.31968 | 0.36261 | 26.2351 | 0.018187 | 0.97908 | 0.35121 | 0.00076019 | 31329.2854 | 0.023803 | 1.6879 | 24.0816 | 27.9194 | 0.80923 | 0.072982
2025-02-07 09:15 | 0.33319 | 0.37793 | 26.2346 | 0.018162 | 0.97908 | 0.36605 | 0.00079232 | 32653.5149 | 0.023803 | 1.6878 | 24.9545 | 28.9311 | 0.84056 | 0.075808
2025-02-07 09:16 | 0.34825 | 0.39501 | 26.2342 | 0.018215 | 0.97908 | 0.3826 | 0.00082813 | 34129.087 | 0.023803 | 1.6878 | 25.9213 | 30.0516 | 0.87922 | 0.079295
2025-02-07 09:17 | 0.34091 | 0.38669 | 26.2346 | 0.018359 | 0.97908 | 0.37454 | 0.00081068 | 33410.2531 | 0.023803 | 1.6878 | 25.451 | 29.5067 | 0.86838 | 0.078317
2025-02-07 09:18 | 0.37682 | 0.42742 | 26.2365 | 0.0184 | 0.97908 | 0.41398 | 0.00089607 | 36929.4934 | 0.023801 | 1.6879 | 27.7399 | 32.1619 | 0.9573 | 0.086336
2025-02-07 09:19 | 0.40577 | 0.46027 | 26.2384 | 0.018505 | 0.97907 | 0.4458 | 0.00096493 | 39767.7288 | 0.0238 | 1.688 | 29.5636 | 34.2778 | 1.033 | 0.093159
2025-02-07 09:20 | 0.37257 | 0.42262 | 26.2404 | 0.018616 | 0.97907 | 0.40932 | 0.00088597 | 36514.0439 | 0.023799 | 1.6881 | 27.4709 | 31.8528 | 0.95828 | 0.086425
2025-02-07 09:21 | 0.37334 | 0.4235 | 26.2423 | 0.018692 | 0.97906 | 0.41017 | 0.00088781 | 36590.1039 | 0.023797 | 1.6882 | 27.5198 | 31.911 | 0.96416 | 0.086955
2025-02-07 09:22 | 0.3938 | 0.44671 | 26.2434 | 0.018835 | 0.97906 | 0.43265 | 0.00093646 | 38595.7814 | 0.023797 | 1.6882 | 28.8121 | 33.4104 | 1.0221 | 0.092179
2025-02-07 09:23 | 0.45326 | 0.51415 | 26.2429 | 0.018826 | 0.97906 | 0.49797 | 0.0010779 | 44422.8843 | 0.023797 | 1.6882 | 32.5157 | 37.7047 | 1.1674 | 0.10529
2025-02-07 09:24 | 0.48916 | 0.55488 | 26.2425 | 0.01881 | 0.97906 | 0.53742 | 0.0011632 | 47941.785 | 0.023797 | 1.6882 | 34.719 | 40.2591 | 1.2539 | 0.11308
2025-02-07 09:25 | 0.45365 | 0.51459 | 26.242 | 0.018931 | 0.97906 | 0.49839 | 0.0010788 | 44460.5025 | 0.023798 | 1.6882 | 32.5395 | 37.7315 | 1.1748 | 0.10596
2025-02-07 09:26 | 0.40577 | 0.46028 | 26.2416 | 0.019074 | 0.97907 | 0.4458 | 0.00096493 | 39768.4016 | 0.023798 | 1.6882 | 29.5636 | 34.2803 | 1.0648 | 0.096033
2025-02-07 09:27 | 0.39728 | 0.45065 | 26.2411 | 0.019141 | 0.97907 | 0.43646 | 0.00094473 | 38935.8536 | 0.023798 | 1.6881 | 29.0306 | 33.6619 | 1.0473 | 0.094451
2025-02-07 09:28 | 0.38724 | 0.43926 | 26.2406 | 0.01909 | 0.97907 | 0.42544 | 0.00092086 | 37951.9579 | 0.023799 | 1.6881 | 28.3986 | 32.9288 | 1.0194 | 0.091937
2025-02-07 09:29 | 0.3884 | 0.44057 | 26.2408 | 0.019096 | 0.97907 | 0.42671 | 0.00092361 | 38065.5053 | 0.023798 | 1.6881 | 28.4717 | 33.0136 | 1.0226 | 0.092229
2025-02-07 09:30 | 0.40732 | 0.46204 | 26.242 | 0.01909 | 0.97906 | 0.44749 | 0.0009686 | 39919.8505 | 0.023798 | 1.6882 | 29.6603 | 34.3929 | 1.0696 | 0.096461
2025-02-07 09:31 | 0.41851 | 0.47474 | 26.2432 | 0.019121 | 0.97906 | 0.45979 | 0.00099522 | 41017.4459 | 0.023797 | 1.6882 | 30.3602 | 35.2054 | 1.0993 | 0.099145
2025-02-07 09:32 | 0.40191 | 0.45591 | 26.2445 | 0.019162 | 0.97906 | 0.44155 | 0.00095574 | 39390.6322 | 0.023796 | 1.6883 | 29.3215 | 34.002 | 1.0602 | 0.095615
2025-02-07 09:33 | 0.40925 | 0.46423 | 26.2457 | 0.019193 | 0.97906 | 0.44961 | 0.00097319 | 40109.8436 | 0.023795 | 1.6883 | 29.7812 | 34.536 | 1.0803 | 0.09743
2025-02-07 09:34 | 0.42508 | 0.48219 | 26.2469 | 0.01921 | 0.97905 | 0.467 | 0.0010108 | 41661.5388 | 0.023794 | 1.6884 | 30.7692 | 35.6828 | 1.1209 | 0.1011
2025-02-07 09:35 | 0.4189 | 0.47519 | 26.2481 | 0.019267 | 0.97905 | 0.46022 | 0.00099614 | 41056.3759 | 0.023793 | 1.6884 | 30.3842 | 35.2374 | 1.1088 | 0.1
2025-02-07 09:36 | 0.42739 | 0.48482 | 26.2482 | 0.019331 | 0.97905 | 0.46955 | 0.0010163 | 41888.8649 | 0.023793 | 1.6885 | 30.9133 | 35.851 | 1.1339 | 0.10227
2025-02-07 09:37 | 0.44901 | 0.50935 | 26.2463 | 0.019331 | 0.97906 | 0.4933 | 0.0010678 | 44007.4509 | 0.023795 | 1.6884 | 32.2535 | 37.4036 | 1.1882 | 0.10716
2025-02-07 09:38 | 0.46793 | 0.5308 | 26.2444 | 0.019305 | 0.97906 | 0.51409 | 0.0011127 | 45861.1148 | 0.023796 | 1.6883 | 33.4188 | 38.7532 | 1.2339 | 0.11128
2025-02-07 09:39 | 0.47758 | 0.54174 | 26.2424 | 0.019389 | 0.97906 | 0.52469 | 0.0011357 | 46806.6068 | 0.023797 | 1.6882 | 34.0108 | 39.4379 | 1.2634 | 0.11394
2025-02-07 09:40 | 0.48723 | 0.55269 | 26.2405 | 0.019396 | 0.97907 | 0.53529 | 0.0011586 | 47752.0775 | 0.023799 | 1.6881 | 34.6011 | 40.1205 | 1.288 | 0.11616
2025-02-07 09:41 | 0.47025 | 0.53341 | 26.2399 | 0.019384 | 0.97907 | 0.51663 | 0.0011182 | 46087.0463 | 0.023799 | 1.6881 | 33.561 | 38.914 | 1.2446 | 0.11225
2025-02-07 09:42 | 0.4714 | 0.53473 | 26.2416 | 0.019453 | 0.97907 | 0.5179 | 0.001121 | 46200.9827 | 0.023798 | 1.6882 | 33.6321 | 38.998 | 1.252 | 0.11291
2025-02-07 09:43 | 0.49959 | 0.56671 | 26.2433 | 0.019527 | 0.97906 | 0.54887 | 0.001188 | 48963.6561 | 0.023797 | 1.6882 | 35.3543 | 40.9966 | 1.3279 | 0.11976
2025-02-07 09:44 | 0.50113 | 0.56847 | 26.2451 | 0.019596 | 0.97906 | 0.55056 | 0.0011917 | 49115.4673 | 0.023795 | 1.6883 | 35.4483 | 41.1073 | 1.3366 | 0.12055
2025-02-07 09:45 | 0.50924 | 0.57767 | 26.2468 | 0.019591 | 0.97905 | 0.55947 | 0.001211 | 49910.5564 | 0.023794 | 1.6884 | 35.9409 | 41.6803 | 1.3568 | 0.12237
2025-02-07 09:46 | 0.52237 | 0.59256 | 26.2481 | 0.019596 | 0.97905 | 0.57389 | 0.0012422 | 51197.4706 | 0.023793 | 1.6884 | 36.7363 | 42.6039 | 1.3904 | 0.12539
2025-02-07 09:47 | 0.51426 | 0.58337 | 26.2487 | 0.019696 | 0.97905 | 0.56499 | 0.0012229 | 50403.0116 | 0.023793 | 1.6885 | 36.2454 | 42.0353 | 1.3769 | 0.12418
2025-02-07 09:48 | 0.51233 | 0.58118 | 26.2494 | 0.019682 | 0.97905 | 0.56286 | 0.0012183 | 50213.9855 | 0.023792 | 1.6885 | 36.1283 | 41.9002 | 1.3711 | 0.12365
2025-02-07 09:49 | 0.51349 | 0.5825 | 26.25 | 0.019617 | 0.97905 | 0.56414 | 0.0012211 | 50327.6804 | 0.023792 | 1.6885 | 36.1985 | 41.9823 | 1.3695 | 0.12351
2025-02-07 09:50 | 0.53241 | 0.60396 | 26.2507 | 0.019722 | 0.97905 | 0.58492 | 0.0012661 | 52182.0392 | 0.023791 | 1.6886 | 37.3426 | 43.3097 | 1.4249 | 0.12851
2025-02-07 09:51 | 0.5436 | 0.61666 | 26.2511 | 0.019861 | 0.97905 | 0.59722 | 0.0012927 | 53279.5273 | 0.023791 | 1.6886 | 38.0169 | 44.0923 | 1.4635 | 0.13199
2025-02-07 09:52 | 0.53086 | 0.60221 | 26.2511 | 0.01993 | 0.97905 | 0.58322 | 0.0012624 | 52030.7896 | 0.023791 | 1.6886 | 37.2494 | 43.2021 | 1.4359 | 0.1295
2025-02-07 09:53 | 0.54939 | 0.62323 | 26.2511 | 0.019925 | 0.97905 | 0.60358 | 0.0013065 | 53847.1369 | 0.023791 | 1.6886 | 38.365 | 44.496 | 1.483 | 0.13375
2025-02-07 09:54 | 0.55982 | 0.63506 | 26.2511 | 0.01993 | 0.97905 | 0.61504 | 0.0013312 | 54868.8335 | 0.023791 | 1.6886 | 38.9902 | 45.2211 | 1.51 | 0.13619
2025-02-07 09:55 | 0.527 | 0.59783 | 26.2511 | 0.019951 | 0.97905 | 0.57898 | 0.0012532 | 51652.3842 | 0.023791 | 1.6886 | 37.0163 | 42.9318 | 1.4276 | 0.12875
2025-02-07 09:56 | 0.53627 | 0.60834 | 26.2511 | 0.019978 | 0.97905 | 0.58916 | 0.0012752 | 52560.5586 | 0.023791 | 1.6886 | 37.5753 | 43.5801 | 1.4533 | 0.13107
2025-02-07 09:57 | 0.54515 | 0.61841 | 26.2511 | 0.020053 | 0.97905 | 0.59892 | 0.0012964 | 53430.893 | 0.023791 | 1.6886 | 38.1098 | 44.2 | 1.4816 | 0.13362
2025-02-07 09:58 | 0.52932 | 0.60046 | 26.2514 | 0.020202 | 0.97905 | 0.58153 | 0.0012587 | 51879.5228 | 0.023791 | 1.6886 | 37.1562 | 43.0943 | 1.4516 | 0.13091
2025-02-07 09:59 | 0.54708 | 0.62061 | 26.2523 | 0.020231 | 0.97904 | 0.60104 | 0.001301 | 53620.4401 | 0.02379 | 1.6886 | 38.2258 | 44.3358 | 1.4998 | 0.13527
2025-02-07 10:00 | 0.54129 | 0.61404 | 26.2531 | 0.020217 | 0.97904 | 0.59468 | 0.0012872 | 53053.0738 | 0.02379 | 1.6887 | 37.8776 | 43.9328 | 1.4838 | 0.13382
2025-02-07 10:01 | 0.52198 | 0.59214 | 26.254 | 0.02021 | 0.97904 | 0.57347 | 0.0012413 | 51161.2606 | 0.023789 | 1.6887 | 36.7129 | 42.5828 | 1.4332 | 0.12926
2025-02-07 10:02 | 0.54824 | 0.62193 | 26.2548 | 0.020352 | 0.97904 | 0.60231 | 0.0013037 | 53734.7086 | 0.023788 | 1.6887 | 38.2954 | 44.4193 | 1.5119 | 0.13636
2025-02-07 10:03 | 0.55634 | 0.63113 | 26.2555 | 0.020476 | 0.97904 | 0.61122 | 0.001323 | 54529.5673 | 0.023788 | 1.6888 | 38.782 | 44.9843 | 1.5425 | 0.13911
2025-02-07 10:04 | 0.53742 | 0.60967 | 26.2558 | 0.020422 | 0.97904 | 0.59044 | 0.001278 | 52675.4236 | 0.023788 | 1.6888 | 37.6451 | 43.6659 | 1.4888 | 0.13427
2025-02-07 10:05 | 0.53549 | 0.60748 | 26.2561 | 0.02038 | 0.97904 | 0.58831 | 0.0012734 | 52486.3021 | 0.023788 | 1.6888 | 37.5288 | 43.5313 | 1.4808 | 0.13355
2025-02-07 10:06 | 0.55596 | 0.63069 | 26.2564 | 0.020434 | 0.97904 | 0.6108 | 0.0013221 | 54491.9958 | 0.023787 | 1.6888 | 38.7588 | 44.9584 | 1.5384 | 0.13874
2025-02-07 10:07 | 0.59032 | 0.66968 | 26.2567 | 0.020503 | 0.97903 | 0.64855 | 0.0014038 | 57859.9999 | 0.023787 | 1.6888 | 40.8102 | 47.3383 | 1.6337 | 0.14734
2025-02-07 10:08 | 0.58144 | 0.6596 | 26.257 | 0.020523 | 0.97903 | 0.63879 | 0.0013827 | 56989.7349 | 0.023787 | 1.6888 | 40.2817 | 46.7256 | 1.6121 | 0.14539
2025-02-07 10:09 | 0.54978 | 0.62369 | 26.2573 | 0.020469 | 0.97903 | 0.60401 | 0.0013074 | 53886.796 | 0.023787 | 1.6889 | 38.3882 | 44.5295 | 1.5248 | 0.13752
2025-02-07 10:10 | 0.53781 | 0.61011 | 26.2578 | 0.020455 | 0.97903 | 0.59086 | 0.0012789 | 52713.823 | 0.023786 | 1.6889 | 37.6684 | 43.695 | 1.4923 | 0.13459
2025-02-07 10:11 | 0.54167 | 0.6145 | 26.2584 | 0.020503 | 0.97903 | 0.5951 | 0.0012881 | 53092.4272 | 0.023786 | 1.6889 | 37.9008 | 43.9653 | 1.506 | 0.13582
2025-02-07 10:12 | 0.53395 | 0.60574 | 26.259 | 0.020604 | 0.97903 | 0.58662 | 0.0012697 | 52335.7687 | 0.023785 | 1.6889 | 37.4357 | 43.4264 | 1.4931 | 0.13466
2025-02-07 10:13 | 0.55364 | 0.62808 | 26.2597 | 0.020639 | 0.97903 | 0.60825 | 0.0013166 | 54265.9118 | 0.023785 | 1.689 | 38.6199 | 44.8008 | 1.5478 | 0.13959
2025-02-07 10:14 | 0.55441 | 0.62896 | 26.2603 | 0.020647 | 0.97903 | 0.6091 | 0.0013184 | 54341.7868 | 0.023785 | 1.689 | 38.6662 | 44.8552 | 1.5504 | 0.13983
2025-02-07 10:15 | 0.55596 | 0.63071 | 26.2607 | 0.020694 | 0.97903 | 0.6108 | 0.0013221 | 54493.2694 | 0.023784 | 1.689 | 38.7588 | 44.963 | 1.5581 | 0.14052
2025-02-07 10:16 | 0.56522 | 0.64122 | 26.2607 | 0.020686 | 0.97903 | 0.62098 | 0.0013441 | 55401.491 | 0.023784 | 1.689 | 39.3137 | 45.6068 | 1.5821 | 0.14269
2025-02-07 10:17 | 0.54437 | 0.61757 | 26.2607 | 0.020666 | 0.97903 | 0.59807 | 0.0012945 | 53357.9946 | 0.023784 | 1.689 | 38.0634 | 44.1563 | 1.5253 | 0.13756
2025-02-07 10:18 | 0.55287 | 0.62721 | 26.2607 | 0.020806 | 0.97903 | 0.6074 | 0.0013147 | 54190.5306 | 0.023784 | 1.689 | 38.5736 | 44.7481 | 1.5583 | 0.14054
2025-02-07 10:19 | 0.5575 | 0.63246 | 26.2607 | 0.020766 | 0.97903 | 0.61249 | 0.0013257 | 54644.64 | 0.023784 | 1.689 | 38.8514 | 45.0704 | 1.5676 | 0.14138
2025-02-07 10:20 | 0.53086 | 0.60224 | 26.2607 | 0.020639 | 0.97903 | 0.58322 | 0.0012624 | 52033.5047 | 0.023784 | 1.689 | 37.2494 | 43.212 | 1.4874 | 0.13415
2025-02-07 10:21 | 0.47295 | 0.53654 | 26.2607 | 0.020702 | 0.97903 | 0.5196 | 0.0011247 | 46357.1223 | 0.023784 | 1.689 | 33.7269 | 39.1256 | 1.3373 | 0.12061
2025-02-07 10:22 | 0.527 | 0.59786 | 26.261 | 0.020706 | 0.97903 | 0.57898 | 0.0012532 | 51655.1522 | 0.023784 | 1.689 | 37.0163 | 42.9418 | 1.482 | 0.13366
2025-02-07 10:23 | 0.57989 | 0.65787 | 26.2616 | 0.020722 | 0.97902 | 0.63709 | 0.001379 | 56839.7853 | 0.023784 | 1.6891 | 40.1897 | 46.624 | 1.6238 | 0.14645
2025-02-07 10:24 | 0.56291 | 0.6386 | 26.2623 | 0.020845 | 0.97902 | 0.61843 | 0.0013386 | 55174.8959 | 0.023783 | 1.6891 | 39.1751 | 45.4476 | 1.5881 | 0.14323
2025-02-07 10:25 | 0.5409 | 0.61363 | 26.2629 | 0.020877 | 0.97902 | 0.59425 | 0.0012863 | 53018.0381 | 0.023783 | 1.6891 | 37.8543 | 43.9161 | 1.5316 | 0.13813
2025-02-07 10:26 | 0.53086 | 0.60225 | 26.2636 | 0.020829 | 0.97902 | 0.58322 | 0.0012624 | 52034.2999 | 0.023782 | 1.6891 | 37.2494 | 43.2149 | 1.5013 | 0.1354
2025-02-07 10:27 | 0.5243 | 0.5948 | 26.264 | 0.020698 | 0.97902 | 0.57601 | 0.0012468 | 51391.0969 | 0.023782 | 1.6892 | 36.853 | 42.7555 | 1.4744 | 0.13297
2025-02-07 10:28 | 0.52468 | 0.59524 | 26.2642 | 0.020674 | 0.97902 | 0.57644 | 0.0012477 | 51429.0012 | 0.023782 | 1.6892 | 36.8763 | 42.7828 | 1.4737 | 0.13291
2025-02-07 10:29 | 0.54244 | 0.61539 | 26.2645 | 0.020798 | 0.97902 | 0.59595 | 0.0012899 | 53169.854 | 0.023782 | 1.6892 | 37.9473 | 44.0255 | 1.53 | 0.13799
2025-02-07 10:30 | 0.5521 | 0.62634 | 26.2647 | 0.020746 | 0.97902 | 0.60655 | 0.0013129 | 54116.0001 | 0.023781 | 1.6892 | 38.5272 | 44.6986 | 1.5519 | 0.13996
2025-02-07 10:31 | 0.53704 | 0.60926 | 26.2649 | 0.020751 | 0.97902 | 0.59001 | 0.0012771 | 52640.171 | 0.023781 | 1.6892 | 37.6218 | 43.6484 | 1.5122 | 0.13638
2025-02-07 10:32 | 0.52546 | 0.59612 | 26.2653 | 0.02081 | 0.97902 | 0.57729 | 0.0012495 | 51504.9775 | 0.023781 | 1.6892 | 36.923 | 42.838 | 1.4855 | 0.13397
2025-02-07 10:33 | 0.52237 | 0.59262 | 26.2659 | 0.020838 | 0.97902 | 0.57389 | 0.0012422 | 51202.4076 | 0.023781 | 1.6892 | 36.7363 | 42.622 | 1.4792 | 0.13341
2025-02-07 10:34 | 0.52584 | 0.59656 | 26.2666 | 0.020857 | 0.97902 | 0.57771 | 0.0012505 | 51543.1803 | 0.02378 | 1.6893 | 36.9463 | 42.8664 | 1.4899 | 0.13437
2025-02-07 10:35 | 0.54206 | 0.61496 | 26.2672 | 0.020772 | 0.97901 | 0.59553 | 0.001289 | 53132.8008 | 0.02378 | 1.6893 | 37.924 | 44.0014 | 1.5272 | 0.13773
2025-02-07 10:36 | 0.5382 | 0.61059 | 26.2679 | 0.020742 | 0.97901 | 0.59128 | 0.0012798 | 52754.5458 | 0.023779 | 1.6893 | 37.6916 | 43.7324 | 1.5148 | 0.13661
2025-02-07 10:37 | 0.53279 | 0.60446 | 26.2687 | 0.020734 | 0.97901 | 0.58535 | 0.001267 | 52224.9623 | 0.023779 | 1.6894 | 37.3658 | 43.3553 | 1.4998 | 0.13526
2025-02-07 10:38 | 0.52507 | 0.5957 | 26.2698 | 0.020884 | 0.97901 | 0.57686 | 0.0012486 | 51468.3779 | 0.023778 | 1.6894 | 36.8996 | 42.8154 | 1.49 | 0.13438
2025-02-07 10:39 | 0.53742 | 0.60972 | 26.2708 | 0.020886 | 0.97901 | 0.59044 | 0.001278 | 52679.7047 | 0.023777 | 1.6895 | 37.6451 | 43.6815 | 1.5234 | 0.13739
2025-02-07 10:40 | 0.54669 | 0.62023 | 26.2719 | 0.020838 | 0.979 | 0.60062 | 0.0013 | 53588.286 | 0.023776 | 1.6895 | 38.2026 | 44.3296 | 1.5447 | 0.13931
2025-02-07 10:41 | 0.55287 | 0.62725 | 26.273 | 0.020829 | 0.979 | 0.6074 | 0.0013147 | 54194.1181 | 0.023776 | 1.6896 | 38.5736 | 44.7611 | 1.5606 | 0.14074
2025-02-07 10:42 | 0.60306 | 0.68419 | 26.2735 | 0.020866 | 0.979 | 0.66254 | 0.0014341 | 59114.1449 | 0.023775 | 1.6896 | 41.5666 | 48.2349 | 1.6974 | 0.15309
2025-02-07 10:43 | 0.60538 | 0.68682 | 26.2733 | 0.020877 | 0.979 | 0.66509 | 0.0014396 | 59341.1461 | 0.023775 | 1.6896 | 41.7039 | 48.3939 | 1.7044 | 0.15372
2025-02-07 10:44 | 0.6297 | 0.71441 | 26.2731 | 0.020943 | 0.979 | 0.69181 | 0.0014974 | 61725.3181 | 0.023776 | 1.6896 | 43.1409 | 50.0612 | 1.7747 | 0.16006
2025-02-07 10:45 | 0.65827 | 0.74683 | 26.2729 | 0.021 | 0.979 | 0.7232 | 0.0015654 | 64525.7783 | 0.023776 | 1.6896 | 44.819 | 52.0082 | 1.8559 | 0.16738
2025-02-07 10:46 | 0.65441 | 0.74245 | 26.2727 | 0.020972 | 0.979 | 0.71896 | 0.0015562 | 64147.2543 | 0.023776 | 1.6895 | 44.5928 | 51.7455 | 1.8431 | 0.16622
2025-02-07 10:47 | 0.58182 | 0.6601 | 26.2732 | 0.020952 | 0.979 | 0.63921 | 0.0013836 | 57032.5795 | 0.023775 | 1.6896 | 40.3047 | 46.7703 | 1.6476 | 0.14859
2025-02-07 10:48 | 0.52198 | 0.59221 | 26.275 | 0.020924 | 0.979 | 0.57347 | 0.0012413 | 51167.0616 | 0.023774 | 1.6896 | 36.7129 | 42.604 | 1.4847 | 0.1339
2025-02-07 10:49 | 0.56175 | 0.63733 | 26.2767 | 0.020962 | 0.97899 | 0.61716 | 0.0013358 | 55065.6537 | 0.023773 | 1.6897 | 39.1058 | 45.3827 | 1.5946 | 0.14381
2025-02-07 10:50 | 0.61001 | 0.69209 | 26.2784 | 0.021057 | 0.97899 | 0.67018 | 0.0014506 | 59796.934 | 0.023772 | 1.6898 | 41.9782 | 48.7182 | 1.7319 | 0.15619
2025-02-07 10:51 | 0.59379 | 0.6737 | 26.2801 | 0.021067 | 0.97899 | 0.65236 | 0.001412 | 58207.9349 | 0.023771 | 1.6899 | 41.0167 | 47.6043 | 1.6892 | 0.15234
2025-02-07 10:52 | 0.57526 | 0.65268 | 26.2813 | 0.021105 | 0.97899 | 0.632 | 0.001368 | 56391.663 | 0.02377 | 1.6899 | 39.9134 | 46.3251 | 1.6422 | 0.14811
2025-02-07 10:53 | 0.59843 | 0.67897 | 26.2817 | 0.021115 | 0.97898 | 0.65745 | 0.0014231 | 58662.6047 | 0.023769 | 1.69 | 41.2918 | 47.9254 | 1.7055 | 0.15382
2025-02-07 10:54 | 0.58144 | 0.65969 | 26.2821 | 0.021067 | 0.97898 | 0.63879 | 0.0013827 | 56997.4756 | 0.023769 | 1.69 | 40.2817 | 46.7535 | 1.656 | 0.14935
2025-02-07 10:55 | 0.58839 | 0.66758 | 26.2826 | 0.02102 | 0.97898 | 0.64642 | 0.0013992 | 57678.8527 | 0.023769 | 1.69 | 40.6954 | 47.2341 | 1.671 | 0.1507
2025-02-07 10:56 | 0.61889 | 0.70219 | 26.283 | 0.021143 | 0.97898 | 0.67993 | 0.0014717 | 60668.9084 | 0.023768 | 1.69 | 42.5032 | 49.3329 | 1.7631 | 0.15901
2025-02-07 10:57 | 0.61425 | 0.69693 | 26.2834 | 0.021267 | 0.97898 | 0.67484 | 0.0014607 | 60214.8836 | 0.023768 | 1.69 | 42.2294 | 49.0156 | 1.7609 | 0.15881
2025-02-07 10:58 | 0.63472 | 0.72015 | 26.2839 | 0.021229 | 0.97898 | 0.69732 | 0.0015094 | 62220.9277 | 0.023768 | 1.69 | 43.4364 | 50.4171 | 1.8131 | 0.16352
2025-02-07 10:59 | 0.62661 | 0.71095 | 26.2843 | 0.021106 | 0.97898 | 0.68842 | 0.0014901 | 61426.2779 | 0.023768 | 1.6901 | 42.9589 | 49.8633 | 1.7808 | 0.16061
2025-02-07 11:00 | 0.56213 | 0.6378 | 26.2847 | 0.021048 | 0.97898 | 0.61758 | 0.0013368 | 55105.8957 | 0.023767 | 1.6901 | 39.1289 | 45.4182 | 1.6026 | 0.14453
2025-02-07 11:01 | 0.55132 | 0.62554 | 26.2852 | 0.021105 | 0.97898 | 0.60571 | 0.0013111 | 54046.2907 | 0.023767 | 1.6901 | 38.4809 | 44.6665 | 1.5776 | 0.14228
2025-02-07 11:02 | 0.57449 | 0.65182 | 26.2856 | 0.021143 | 0.97898 | 0.63116 | 0.0013661 | 56317.2755 | 0.023767 | 1.6901 | 39.8673 | 46.2763 | 1.6433 | 0.1482
2025-02-07 11:03 | 0.62622 | 0.71052 | 26.286 | 0.021087 | 0.97898 | 0.68799 | 0.0014892 | 61389.0027 | 0.023766 | 1.6901 | 42.9361 | 49.8389 | 1.7783 | 0.16038
2025-02-07 11:04 | 0.63974 | 0.72585 | 26.2864 | 0.02119 | 0.97897 | 0.70284 | 0.0015213 | 62713.817 | 0.023766 | 1.6902 | 43.7317 | 50.7629 | 1.8235 | 0.16446
2025-02-07 11:05 | 0.62854 | 0.71315 | 26.2869 | 0.021286 | 0.97897 | 0.69054 | 0.0014947 | 61616.3727 | 0.023766 | 1.6902 | 43.0726 | 49.9984 | 1.8014 | 0.16246
2025-02-07 11:06 | 0.649 | 0.73637 | 26.2873 | 0.021172 | 0.97897 | 0.71302 | 0.0015433 | 63622.4604 | 0.023765 | 1.6902 | 44.2759 | 51.3956 | 1.8469 | 0.16657
2025-02-07 11:07 | 0.65672 | 0.74514 | 26.2881 | 0.021096 | 0.97897 | 0.7215 | 0.0015617 | 64379.6935 | 0.023765 | 1.6902 | 44.7285 | 51.922 | 1.861 | 0.16784
2025-02-07 11:08 | 0.65248 | 0.74032 | 26.2894 | 0.02121 | 0.97897 | 0.71684 | 0.0015516 | 63963.8082 | 0.023764 | 1.6903 | 44.4796 | 51.6347 | 1.8597 | 0.16772
2025-02-07 11:09 | 0.65595 | 0.74427 | 26.2907 | 0.021372 | 0.97897 | 0.72065 | 0.0015599 | 64304.8919 | 0.023763 | 1.6904 | 44.6833 | 51.8727 | 1.8834 | 0.16986
2025-02-07 11:10 | 0.64167 | 0.72807 | 26.292 | 0.021486 | 0.97896 | 0.70496 | 0.0015259 | 62904.9297 | 0.023762 | 1.6904 | 43.8451 | 50.9012 | 1.8545 | 0.16726
2025-02-07 11:11 | 0.6158 | 0.69872 | 26.2932 | 0.021554 | 0.97896 | 0.67654 | 0.0014644 | 60369.4702 | 0.023761 | 1.6905 | 42.3207 | 49.133 | 1.7894 | 0.16138
2025-02-07 11:12 | 0.62159 | 0.70529 | 26.2936 | 0.021629 | 0.97896 | 0.6829 | 0.0014781 | 60937.3378 | 0.023761 | 1.6905 | 42.6628 | 49.5305 | 1.8117 | 0.16339
2025-02-07 11:13 | 0.65248 | 0.74034 | 26.2928 | 0.021668 | 0.97896 | 0.71684 | 0.0015516 | 63964.9829 | 0.023762 | 1.6904 | 44.4796 | 51.6389 | 1.9 | 0.17136
2025-02-07 11:14 | 0.67719 | 0.76837 | 26.2919 | 0.021639 | 0.97896 | 0.74398 | 0.0016104 | 66387.0169 | 0.023762 | 1.6904 | 45.9245 | 53.3152 | 1.9653 | 0.17725
2025-02-07 11:15 | 0.68491 | 0.77713 | 26.2911 | 0.021563 | 0.97897 | 0.75247 | 0.0016287 | 67143.6839 | 0.023763 | 1.6904 | 46.3745 | 53.8365 | 1.9795 | 0.17852
2025-02-07 11:16 | 0.66174 | 0.75084 | 26.2902 | 0.021468 | 0.97897 | 0.72702 | 0.0015736 | 64872.4575 | 0.023763 | 1.6903 | 45.0223 | 52.2657 | 1.9076 | 0.17204
2025-02-07 11:17 | 0.66329 | 0.75259 | 26.2904 | 0.021486 | 0.97897 | 0.72871 | 0.0015773 | 65023.9271 | 0.023763 | 1.6903 | 45.1127 | 52.3709 | 1.9135 | 0.17257
2025-02-07 11:18 | 0.65402 | 0.74209 | 26.2921 | 0.021497 | 0.97896 | 0.71853 | 0.0015553 | 64116.156 | 0.023762 | 1.6904 | 44.5702 | 51.7432 | 1.8892 | 0.17038
2025-02-07 11:19 | 0.63896 | 0.72501 | 26.2938 | 0.021534 | 0.97896 | 0.70199 | 0.0015195 | 62640.6279 | 0.023761 | 1.6905 | 43.6863 | 50.7191 | 1.8513 | 0.16697
2025-02-07 11:20 | 0.63124 | 0.71625 | 26.2956 | 0.021515 | 0.97896 | 0.69351 | 0.0015011 | 61884.2161 | 0.02376 | 1.6906 | 43.2319 | 50.1936 | 1.8287 | 0.16492
2025-02-07 11:21 | 0.65286 | 0.74079 | 26.2973 | 0.02142 | 0.97895 | 0.71726 | 0.0015525 | 64004.3919 | 0.023758 | 1.6906 | 44.5023 | 51.6707 | 1.8796 | 0.16951
2025-02-07 11:22 | 0.68143 | 0.77321 | 26.2983 | 0.021325 | 0.97895 | 0.74865 | 0.0016205 | 66805.6779 | 0.023758 | 1.6907 | 46.1721 | 53.6107 | 1.9487 | 0.17575
2025-02-07 11:23 | 0.68529 | 0.7776 | 26.2985 | 0.021429 | 0.97895 | 0.75289 | 0.0016296 | 67184.2361 | 0.023757 | 1.6907 | 46.3969 | 53.8721 | 1.9686 | 0.17754
2025-02-07 11:24 | 0.64669 | 0.73379 | 26.2987 | 0.021497 | 0.97895 | 0.71047 | 0.0015378 | 63399.2609 | 0.023757 | 1.6907 | 44.1399 | 51.2516 | 1.8695 | 0.16861
2025-02-07 11:25 | 0.63665 | 0.7224 | 26.2988 | 0.021563 | 0.97895 | 0.69945 | 0.001514 | 62415.2046 | 0.023757 | 1.6907 | 43.55 | 50.5669 | 1.8477 | 0.16664
2025-02-07 11:26 | 0.65248 | 0.74036 | 26.299 | 0.02162 | 0.97895 | 0.71684 | 0.0015516 | 63967.122 | 0.023757 | 1.6907 | 44.4796 | 51.6464 | 1.8962 | 0.17101
2025-02-07 11:27 | 0.63703 | 0.72284 | 26.2991 | 0.021563 | 0.97895 | 0.69987 | 0.0015149 | 62453.1598 | 0.023757 | 1.6907 | 43.5727 | 50.5936 | 1.8489 | 0.16674
2025-02-07 11:28 | 0.6629 | 0.75219 | 26.2993 | 0.021582 | 0.97895 | 0.72829 | 0.0015764 | 64989.1914 | 0.023757 | 1.6907 | 45.0901 | 52.3556 | 1.9214 | 0.17329
2025-02-07 11:29 | 0.68993 | 0.78286 | 26.2995 | 0.021621 | 0.97895 | 0.75798 | 0.0016406 | 67638.8193 | 0.023757 | 1.6907 | 46.6666 | 54.1865 | 1.999 | 0.18028
2025-02-07 11:30 | 0.71078 | 0.80652 | 26.3 | 0.021706 | 0.97895 | 0.78088 | 0.0016902 | 69682.9056 | 0.023756 | 1.6908 | 47.8768 | 55.5923 | 2.0641 | 0.18616
2025-02-07 11:31 | 0.71155 | 0.80739 | 26.3004 | 0.021763 | 0.97895 | 0.78173 | 0.0016921 | 69758.7682 | 0.023756 | 1.6908 | 47.9215 | 55.6448 | 2.0718 | 0.18685
2025-02-07 11:32 | 0.70498 | 0.79995 | 26.3008 | 0.02182 | 0.97895 | 0.77452 | 0.0016765 | 69115.4692 | 0.023756 | 1.6908 | 47.5411 | 55.2036 | 2.0591 | 0.18571
2025-02-07 11:33 | 0.69186 | 0.78505 | 26.3012 | 0.021887 | 0.97894 | 0.7601 | 0.0016452 | 67828.7005 | 0.023756 | 1.6908 | 46.7788 | 54.319 | 2.0291 | 0.183
2025-02-07 11:34 | 0.70035 | 0.7947 | 26.3022 | 0.021906 | 0.97894 | 0.76943 | 0.0016654 | 68661.7759 | 0.023755 | 1.6909 | 47.2723 | 54.8933 | 2.0545 | 0.18529
2025-02-07 11:35 | 0.69263 | 0.78594 | 26.3039 | 0.021935 | 0.97894 | 0.76095 | 0.0016471 | 67905.3851 | 0.023754 | 1.6909 | 46.8237 | 54.3746 | 2.0358 | 0.1836
2025-02-07 11:36 | 0.65557 | 0.74389 | 26.3056 | 0.021954 | 0.97894 | 0.72023 | 0.0015589 | 64272.2488 | 0.023752 | 1.691 | 44.6607 | 51.8648 | 1.9345 | 0.17446
2025-02-07 11:37 | 0.6795 | 0.77106 | 26.3074 | 0.022011 | 0.97893 | 0.74653 | 0.0016159 | 66619.6751 | 0.023751 | 1.6911 | 46.0595 | 53.4916 | 2.0065 | 0.18096
2025-02-07 11:38 | 0.7212 | 0.81838 | 26.3091 | 0.022163 | 0.97893 | 0.79234 | 0.001715 | 70708.3567 | 0.02375 | 1.6912 | 48.48 | 56.3049 | 2.1374 | 0.19277
2025-02-07 11:39 | 0.76251 | 0.86527 | 26.3104 | 0.022183 | 0.97893 | 0.83772 | 0.0018133 | 74759.1019 | 0.023749 | 1.6912 | 50.8588 | 59.0695 | 2.255 | 0.20337
2025-02-07 11:40 | 0.7405 | 0.8403 | 26.3112 | 0.022116 | 0.97892 | 0.81355 | 0.0017609 | 72601.7972 | 0.023749 | 1.6913 | 49.5939 | 57.6014 | 2.1869 | 0.19723
2025-02-07 11:41 | 0.71927 | 0.81621 | 26.3119 | 0.022126 | 0.97892 | 0.79022 | 0.0017104 | 70520.182 | 0.023748 | 1.6913 | 48.3684 | 56.1791 | 2.1286 | 0.19197
2025-02-07 11:42 | 0.72738 | 0.82541 | 26.3127 | 0.022201 | 0.97892 | 0.79912 | 0.0017297 | 71315.3915 | 0.023747 | 1.6913 | 48.8369 | 56.7243 | 2.1586 | 0.19468
2025-02-07 11:43 | 0.72931 | 0.8276 | 26.3135 | 0.022212 | 0.97892 | 0.80124 | 0.0017343 | 71504.9544 | 0.023747 | 1.6914 | 48.9484 | 56.8547 | 2.1651 | 0.19527
2025-02-07 11:44 | 0.73008 | 0.82848 | 26.3142 | 0.022306 | 0.97892 | 0.80209 | 0.0017361 | 71580.958 | 0.023746 | 1.6914 | 48.9929 | 56.9075 | 2.1766 | 0.1963
2025-02-07 11:45 | 0.70035 | 0.79475 | 26.315 | 0.022412 | 0.97892 | 0.76943 | 0.0016654 | 68666.5231 | 0.023746 | 1.6914 | 47.2723 | 54.9099 | 2.1027 | 0.18963
2025-02-07 11:46 | 0.6741 | 0.76496 | 26.3158 | 0.022488 | 0.97892 | 0.74059 | 0.001603 | 66092.7623 | 0.023745 | 1.6915 | 45.7443 | 53.1361 | 2.035 | 0.18353
2025-02-07 11:47 | 0.69803 | 0.79213 | 26.3167 | 0.022498 | 0.97891 | 0.76689 | 0.0016599 | 68440.0162 | 0.023745 | 1.6915 | 47.1378 | 54.7559 | 2.1042 | 0.18977
2025-02-07 11:48 | 0.70305 | 0.79783 | 26.3175 | 0.022478 | 0.97891 | 0.7724 | 0.0016719 | 68932.4392 | 0.023744 | 1.6916 | 47.4291 | 55.0954 | 2.1167 | 0.1909
2025-02-07 11:49 | 0.70846 | 0.80397 | 26.3184 | 0.022479 | 0.97891 | 0.77834 | 0.0016847 | 69462.7191 | 0.023743 | 1.6916 | 47.7426 | 55.4606 | 2.1322 | 0.1923
2025-02-07 11:50 | 0.71579 | 0.81229 | 26.3192 | 0.022536 | 0.97891 | 0.7864 | 0.0017022 | 70182.278 | 0.023743 | 1.6916 | 48.1674 | 55.9553 | 2.1586 | 0.19468
2025-02-07 11:51 | 0.70151 | 0.79609 | 26.3202 | 0.022631 | 0.97891 | 0.7707 | 0.0016682 | 68782.0138 | 0.023742 | 1.6917 | 47.3395 | 54.9948 | 2.1268 | 0.19181
2025-02-07 11:52 | 0.70035 | 0.79478 | 26.3213 | 0.022669 | 0.9789 | 0.76943 | 0.0016654 | 68668.847 | 0.023741 | 1.6917 | 47.2723 | 54.9181 | 2.1272 | 0.19185
2025-02-07 11:53 | 0.69495 | 0.78865 | 26.3223 | 0.022669 | 0.9789 | 0.76349 | 0.0016526 | 68139.2739 | 0.023741 | 1.6918 | 46.9584 | 54.5548 | 2.1117 | 0.19045
2025-02-07 11:54 | 0.70074 | 0.79523 | 26.3234 | 0.022584 | 0.9789 | 0.76986 | 0.0016664 | 68707.5003 | 0.02374 | 1.6918 | 47.2947 | 54.9469 | 2.1204 | 0.19124
2025-02-07 11:55 | 0.77255 | 0.87672 | 26.3245 | 0.022612 | 0.9789 | 0.84875 | 0.0018371 | 75749.04 | 0.023739 | 1.6919 | 51.4341 | 59.7576 | 2.3281 | 0.20997
2025-02-07 11:56 | 0.85015 | 0.9648 | 26.3255 | 0.022783 | 0.9789 | 0.93401 | 0.0020217 | 83358.4571 | 0.023738 | 1.6919 | 55.8472 | 64.8864 | 2.5675 | 0.23156
2025-02-07 11:57 | 0.78954 | 0.89601 | 26.3263 | 0.022775 | 0.97889 | 0.86741 | 0.0018775 | 77415.4557 | 0.023738 | 1.6919 | 52.4053 | 60.8886 | 2.3936 | 0.21587
2025-02-07 11:58 | 0.74089 | 0.84081 | 26.3272 | 0.022717 | 0.97889 | 0.81397 | 0.0017618 | 72645.94 | 0.023737 | 1.692 | 49.6162 | 57.6491 | 2.2484 | 0.20278
2025-02-07 11:59 | 0.80228 | 0.91048 | 26.328 | 0.022688 | 0.97889 | 0.88141 | 0.0019078 | 78665.4331 | 0.023737 | 1.692 | 53.1317 | 61.7351 | 2.421 | 0.21834
2025-02-07 12:00 | 0.82699 | 0.93853 | 26.3289 | 0.02264 | 0.97889 | 0.90856 | 0.0019666 | 81088.6139 | 0.023736 | 1.6921 | 54.536 | 63.3681 | 2.4861 | 0.22421
2025-02-07 12:01 | 0.77062 | 0.87456 | 26.3298 | 0.022536 | 0.97889 | 0.84663 | 0.0018325 | 75561.9505 | 0.023735 | 1.6921 | 51.3236 | 59.6367 | 2.3152 | 0.2088
2025-02-07 12:02 | 0.77718 | 0.88201 | 26.3309 | 0.022479 | 0.97888 | 0.85384 | 0.0018481 | 76205.9567 | 0.023735 | 1.6922 | 51.6993 | 60.0748 | 2.3279 | 0.20995
2025-02-07 12:03 | 0.79957 | 0.90743 | 26.332 | 0.022621 | 0.97888 | 0.87844 | 0.0019014 | 78402.1143 | 0.023734 | 1.6922 | 52.9778 | 61.562 | 2.4063 | 0.21702
2025-02-07 12:04 | 0.80073 | 0.90875 | 26.3331 | 0.022688 | 0.97888 | 0.87971 | 0.0019041 | 78516.1432 | 0.023733 | 1.6923 | 53.0438 | 61.6403 | 2.4169 | 0.21797
2025-02-07 12:05 | 0.79649 | 0.90394 | 26.3341 | 0.022556 | 0.97888 | 0.87505 | 0.001894 | 78100.1625 | 0.023732 | 1.6923 | 52.8017 | 61.3606 | 2.3908 | 0.21562
2025-02-07 12:06 | 0.77332 | 0.87765 | 26.3347 | 0.022592 | 0.97888 | 0.8496 | 0.001839 | 75828.9285 | 0.023732 | 1.6923 | 51.4783 | 59.8234 | 2.3289 | 0.21003
2025-02-07 12:07 | 0.77332 | 0.87765 | 26.3345 | 0.022499 | 0.97888 | 0.8496 | 0.001839 | 75828.842 | 0.023732 | 1.6923 | 51.4783 | 59.8231 | 2.3193 | 0.20917
2025-02-07 12:08 | 0.79803 | 0.90569 | 26.3342 | 0.022469 | 0.97888 | 0.87675 | 0.0018977 | 78251.6404 | 0.023732 | 1.6923 | 52.8898 | 61.463 | 2.386 | 0.21519
2025-02-07 12:09 | 0.80421 | 0.9127 | 26.334 | 0.02264 | 0.97888 | 0.88353 | 0.0019124 | 78857.2677 | 0.023732 | 1.6923 | 53.2416 | 61.8717 | 2.4217 | 0.21841
2025-02-07 12:10 | 0.79957 | 0.90744 | 26.3338 | 0.022661 | 0.97888 | 0.87844 | 0.0019014 | 78402.888 | 0.023732 | 1.6923 | 52.9778 | 61.5647 | 2.4108 | 0.21742
2025-02-07 12:11 | 0.80459 | 0.91314 | 26.3347 | 0.022849 | 0.97888 | 0.88396 | 0.0019133 | 78895.4052 | 0.023732 | 1.6923 | 53.2636 | 61.8981 | 2.4453 | 0.22053
2025-02-07 12:12 | 0.80961 | 0.91885 | 26.337 | 0.023002 | 0.97887 | 0.88947 | 0.0019253 | 79388.5655 | 0.02373 | 1.6924 | 53.5493 | 62.2335 | 2.4762 | 0.22332
2025-02-07 12:13 | 0.77448 | 0.87899 | 26.3394 | 0.022718 | 0.97887 | 0.85087 | 0.0018417 | 75944.4402 | 0.023729 | 1.6925 | 51.5446 | 59.9072 | 2.3455 | 0.21154
2025-02-07 12:14 | 0.75402 | 0.85577 | 26.3418 | 0.02244 | 0.97886 | 0.82839 | 0.0017931 | 73938.8764 | 0.023727 | 1.6926 | 50.3712 | 58.5467 | 2.2591 | 0.20375
2025-02-07 12:15 | 0.75517 | 0.8571 | 26.3441 | 0.022269 | 0.97886 | 0.82966 | 0.0017958 | 74053.4006 | 0.023725 | 1.6927 | 50.4378 | 58.6273 | 2.2453 | 0.2025
2025-02-07 12:16 | 0.78259 | 0.88822 | 26.3461 | 0.022135 | 0.97885 | 0.85978 | 0.001861 | 76742.2684 | 0.023724 | 1.6928 | 52.0083 | 60.4558 | 2.3084 | 0.20819
2025-02-07 12:17 | 0.83741 | 0.95045 | 26.3476 | 0.022039 | 0.97885 | 0.92001 | 0.0019914 | 82119.0601 | 0.023723 | 1.6929 | 55.1267 | 64.0829 | 2.4501 | 0.22097
2025-02-07 12:18 | 0.79687 | 0.90445 | 26.3491 | 0.021745 | 0.97885 | 0.87547 | 0.001895 | 78144.3606 | 0.023722 | 1.693 | 52.8237 | 61.408 | 2.3069 | 0.20806
2025-02-07 12:19 | 0.78915 | 0.89569 | 26.3506 | 0.021459 | 0.97884 | 0.86699 | 0.0018766 | 77387.774 | 0.023721 | 1.693 | 52.3832 | 60.8981 | 2.2558 | 0.20345
2025-02-07 12:20 | 0.74938 | 0.85056 | 26.3521 | 0.021382 | 0.97884 | 0.8233 | 0.001782 | 73488.6918 | 0.02372 | 1.6931 | 50.105 | 58.2515 | 2.1407 | 0.19307
2025-02-07 12:21 | 0.72429 | 0.82208 | 26.3529 | 0.021354 | 0.97884 | 0.79573 | 0.0017224 | 71028.0156 | 0.023719 | 1.6931 | 48.6585 | 56.571 | 2.0703 | 0.18671
2025-02-07 12:22 | 0.7324 | 0.83128 | 26.3527 | 0.02139 | 0.97884 | 0.80464 | 0.0017416 | 71823.0209 | 0.023719 | 1.6931 | 49.1266 | 57.1149 | 2.0957 | 0.18901
2025-02-07 12:23 | 0.71927 | 0.81638 | 26.3525 | 0.021258 | 0.97884 | 0.79022 | 0.0017104 | 70535.6506 | 0.023719 | 1.6931 | 48.3684 | 56.2331 | 2.0475 | 0.18466
2025-02-07 12:24 | 0.72159 | 0.81901 | 26.3523 | 0.021115 | 0.97884 | 0.79276 | 0.0017159 | 70762.7365 | 0.023719 | 1.6931 | 48.5023 | 56.3885 | 2.0399 | 0.18397
2025-02-07 12:25 | 0.70383 | 0.79885 | 26.3521 | 0.021125 | 0.97884 | 0.77325 | 0.0016737 | 69021.0368 | 0.02372 | 1.6931 | 47.4739 | 55.1926 | 1.9933 | 0.17977
2025-02-07 12:26 | 0.66136 | 0.75065 | 26.3522 | 0.021257 | 0.97884 | 0.72659 | 0.0015727 | 64856.3507 | 0.023719 | 1.6931 | 44.9997 | 52.3163 | 1.8912 | 0.17057
2025-02-07 12:27 | 0.5687 | 0.64548 | 26.3528 | 0.021362 | 0.97884 | 0.62479 | 0.0013524 | 55769.841 | 0.023719 | 1.6931 | 39.5215 | 45.948 | 1.6477 | 0.1486
2025-02-07 12:28 | 0.50538 | 0.57362 | 26.3535 | 0.021325 | 0.97884 | 0.55523 | 0.0012018 | 49560.7446 | 0.023719 | 1.6932 | 35.7065 | 41.5133 | 1.4709 | 0.13265
2025-02-07 12:29 | 0.5575 | 0.63278 | 26.3541 | 0.0214 | 0.97884 | 0.61249 | 0.0013257 | 54672.242 | 0.023718 | 1.6932 | 38.8514 | 45.1704 | 1.6199 | 0.14609
2025-02-07 12:30 | 0.59997 | 0.68099 | 26.3548 | 0.021449 | 0.97884 | 0.65915 | 0.0014267 | 58837.2311 | 0.023718 | 1.6932 | 41.3834 | 48.115 | 1.7404 | 0.15696
2025-02-07 12:31 | 0.60306 | 0.6845 | 26.356 | 0.021458 | 0.97883 | 0.66254 | 0.0014341 | 59140.5334 | 0.023717 | 1.6933 | 41.5666 | 48.3294 | 1.7497 | 0.1578
2025-02-07 12:32 | 0.59341 | 0.67355 | 26.3582 | 0.02142 | 0.97883 | 0.65194 | 0.0014111 | 58194.6567 | 0.023715 | 1.6934 | 40.9938 | 47.6658 | 1.7202 | 0.15514
2025-02-07 12:33 | 0.5382 | 0.61089 | 26.3603 | 0.021325 | 0.97883 | 0.59128 | 0.0012798 | 52780.9316 | 0.023714 | 1.6935 | 37.6916 | 43.8284 | 1.5614 | 0.14082
2025-02-07 12:34 | 0.53279 | 0.60476 | 26.3625 | 0.021259 | 0.97882 | 0.58535 | 0.001267 | 52251.4578 | 0.023712 | 1.6936 | 37.3658 | 43.4518 | 1.5419 | 0.13906
2025-02-07 12:35 | 0.53086 | 0.60258 | 26.3646 | 0.021409 | 0.97882 | 0.58322 | 0.0012624 | 52062.7449 | 0.023711 | 1.6937 | 37.2494 | 43.3186 | 1.5476 | 0.13957
2025-02-07 12:36 | 0.49534 | 0.56226 | 26.3662 | 0.021439 | 0.97881 | 0.5442 | 0.0011779 | 48579.6863 | 0.02371 | 1.6937 | 35.0957 | 40.8155 | 1.4514 | 0.1309
2025-02-07 12:37 | 0.46098 | 0.52326 | 26.367 | 0.021326 | 0.97881 | 0.50645 | 0.0010962 | 45209.9669 | 0.023709 | 1.6938 | 32.9915 | 38.3691 | 1.3486 | 0.12163
2025-02-07 12:38 | 0.49071 | 0.55701 | 26.3677 | 0.021486 | 0.97881 | 0.53911 | 0.0011669 | 48125.7178 | 0.023708 | 1.6938 | 34.8132 | 40.4885 | 1.4417 | 0.13002
2025-02-07 12:39 | 0.50577 | 0.5741 | 26.3685 | 0.021592 | 0.97881 | 0.55565 | 0.0012027 | 49602.637 | 0.023708 | 1.6938 | 35.7299 | 41.5554 | 1.491 | 0.13447
2025-02-07 12:40 | 0.48492 | 0.55044 | 26.3693 | 0.021601 | 0.97881 | 0.53275 | 0.0011531 | 47558.1455 | 0.023707 | 1.6939 | 34.4596 | 40.0786 | 1.4333 | 0.12927
2025-02-07 12:41 | 0.4633 | 0.5259 | 26.37 | 0.021677 | 0.97881 | 0.509 | 0.0011017 | 45437.9066 | 0.023707 | 1.6939 | 33.1341 | 38.5377 | 1.3775 | 0.12423
2025-02-07 12:42 | 0.46137 | 0.52371 | 26.3708 | 0.021744 | 0.9788 | 0.50688 | 0.0010971 | 45248.769 | 0.023706 | 1.6939 | 33.0153 | 38.4002 | 1.3763 | 0.12412
2025-02-07 12:43 | 0.44515 | 0.50531 | 26.3717 | 0.021735 | 0.9788 | 0.48906 | 0.0010586 | 43658.6463 | 0.023706 | 1.694 | 32.0149 | 37.2375 | 1.3299 | 0.11994
2025-02-07 12:44 | 0.43589 | 0.49479 | 26.3728 | 0.021801 | 0.9788 | 0.47888 | 0.0010365 | 42750.1288 | 0.023705 | 1.694 | 31.4409 | 36.5708 | 1.3076 | 0.11793
2025-02-07 12:45 | 0.4494 | 0.51014 | 26.3738 | 0.02183 | 0.9788 | 0.49373 | 0.0010687 | 44075.6768 | 0.023704 | 1.6941 | 32.2774 | 37.5447 | 1.3478 | 0.12156
2025-02-07 12:46 | 0.46484 | 0.52767 | 26.3749 | 0.021754 | 0.9788 | 0.51069 | 0.0011054 | 45590.5701 | 0.023703 | 1.6941 | 33.229 | 38.6526 | 1.3869 | 0.12508
2025-02-07 12:47 | 0.47295 | 0.53688 | 26.376 | 0.021715 | 0.97879 | 0.5196 | 0.0011247 | 46386.0248 | 0.023703 | 1.6942 | 33.7269 | 39.2327 | 1.4074 | 0.12693
2025-02-07 12:48 | 0.46561 | 0.52855 | 26.3767 | 0.02163 | 0.97879 | 0.51154 | 0.0011072 | 45666.7443 | 0.023702 | 1.6942 | 33.2765 | 38.7095 | 1.3813 | 0.12458
2025-02-07 12:49 | 0.4799 | 0.54477 | 26.3769 | 0.021601 | 0.97879 | 0.52724 | 0.0011412 | 47067.8512 | 0.023702 | 1.6942 | 34.1526 | 39.7288 | 1.4195 | 0.12802
2025-02-07 12:50 | 0.45017 | 0.51102 | 26.3771 | 0.021592 | 0.97879 | 0.49457 | 0.0010705 | 44152.1953 | 0.023702 | 1.6942 | 32.3251 | 37.6031 | 1.3354 | 0.12044
2025-02-07 12:51 | 0.43743 | 0.49656 | 26.3773 | 0.021544 | 0.97879 | 0.48058 | 0.0010402 | 42902.6535 | 0.023702 | 1.6942 | 31.5367 | 36.6862 | 1.2967 | 0.11695
2025-02-07 12:52 | 0.48994 | 0.55616 | 26.3775 | 0.021525 | 0.97879 | 0.53826 | 0.0011651 | 48052.5441 | 0.023702 | 1.6942 | 34.7661 | 40.4431 | 1.4426 | 0.1301
2025-02-07 12:53 | 0.50654 | 0.57501 | 26.3781 | 0.021582 | 0.97879 | 0.5565 | 0.0012046 | 49680.9564 | 0.023701 | 1.6943 | 35.7768 | 41.6194 | 1.4929 | 0.13464
2025-02-07 12:54 | 0.50924 | 0.57808 | 26.3792 | 0.021734 | 0.97879 | 0.55947 | 0.001211 | 49946.3108 | 0.0237 | 1.6943 | 35.9409 | 41.8114 | 1.511 | 0.13627
2025-02-07 12:55 | 0.4992 | 0.56669 | 26.3803 | 0.021726 | 0.97878 | 0.54844 | 0.0011871 | 48962.0579 | 0.0237 | 1.6944 | 35.3308 | 41.1027 | 1.4823 | 0.13368
2025-02-07 12:56 | 0.44708 | 0.50753 | 26.3813 | 0.021867 | 0.97878 | 0.49118 | 0.0010632 | 43850.2657 | 0.023699 | 1.6944 | 32.1342 | 37.3848 | 1.3438 | 0.1212
2025-02-07 12:57 | 0.42894 | 0.48693 | 26.3824 | 0.022002 | 0.97878 | 0.47125 | 0.00102 | 42070.7506 | 0.023698 | 1.6945 | 31.0094 | 36.0771 | 1.3 | 0.11724
2025-02-07 12:58 | 0.43975 | 0.4992 | 26.3836 | 0.022002 | 0.97878 | 0.48312 | 0.0010457 | 43131.3096 | 0.023697 | 1.6945 | 31.6803 | 36.8587 | 1.3312 | 0.12005
2025-02-07 12:59 | 0.46059 | 0.52288 | 26.3849 | 0.022116 | 0.97878 | 0.50603 | 0.0010953 | 45176.4806 | 0.023696 | 1.6946 | 32.9678 | 38.3578 | 1.3982 | 0.1261
2025-02-07 13:00 | 0.50577 | 0.57416 | 26.3862 | 0.022191 | 0.97877 | 0.55565 | 0.0012027 | 49607.3789 | 0.023695 | 1.6946 | 35.7299 | 41.5728 | 1.5331 | 0.13827
2025-02-07 13:01 | 0.59418 | 0.67453 | 26.3874 | 0.021879 | 0.97877 | 0.65279 | 0.001413 | 58279.609 | 0.023695 | 1.6947 | 41.0397 | 47.7523 | 1.7608 | 0.1588
2025-02-07 13:02 | 0.6212 | 0.70522 | 26.3887 | 0.021725 | 0.97877 | 0.68248 | 0.0014772 | 60930.8286 | 0.023694 | 1.6947 | 42.64 | 49.6159 | 1.8236 | 0.16446
2025-02-07 13:03 | 0.58298 | 0.66183 | 26.3891 | 0.021735 | 0.97877 | 0.64049 | 0.0013863 | 57181.9441 | 0.023693 | 1.6948 | 40.3737 | 46.9793 | 1.7181 | 0.15495
2025-02-07 13:04 | 0.59843 | 0.67936 | 26.3883 | 0.021858 | 0.97877 | 0.65745 | 0.0014231 | 58696.4244 | 0.023694 | 1.6947 | 41.2918 | 48.0466 | 1.771 | 0.15973
2025-02-07 13:05 | 0.68877 | 0.78191 | 26.3874 | 0.022068 | 0.97877 | 0.75671 | 0.0016379 | 67557.3773 | 0.023695 | 1.6947 | 46.5992 | 54.2211 | 2.0422 | 0.18418
2025-02-07 13:06 | 0.72622 | 0.82442 | 26.3865 | 0.022145 | 0.97877 | 0.79785 | 0.001727 | 71230.29 | 0.023695 | 1.6946 | 48.77 | 56.7459 | 2.1545 | 0.19431
2025-02-07 13:07 | 0.71618 | 0.81303 | 26.3857 | 0.02223 | 0.97877 | 0.78682 | 0.0017031 | 70245.3862 | 0.023696 | 1.6946 | 48.1897 | 56.0695 | 2.1345 | 0.1925
2025-02-07 13:08 | 0.73471 | 0.83406 | 26.3855 | 0.022345 | 0.97877 | 0.80718 | 0.0017471 | 72062.9656 | 0.023696 | 1.6946 | 49.2602 | 57.3147 | 2.1979 | 0.19822
2025-02-07 13:09 | 0.78567 | 0.89192 | 26.3861 | 0.022411 | 0.97877 | 0.86317 | 0.0018683 | 77061.8231 | 0.023696 | 1.6946 | 52.1848 | 60.7184 | 2.3486 | 0.21181
2025-02-07 13:10 | 0.80768 | 0.9169 | 26.3867 | 0.022346 | 0.97877 | 0.88735 | 0.0019207 | 79220.5893 | 0.023695 | 1.6947 | 53.4394 | 62.1792 | 2.4036 | 0.21678
2025-02-07 13:11 | 0.76598 | 0.86957 | 26.3874 | 0.022402 | 0.97877 | 0.84154 | 0.0018215 | 75131.0697 | 0.023695 | 1.6947 | 51.0581 | 59.4093 | 2.2921 | 0.20672
2025-02-07 13:12 | 0.75363 | 0.85555 | 26.388 | 0.022507 | 0.97877 | 0.82797 | 0.0017921 | 73919.5356 | 0.023694 | 1.6947 | 50.3491 | 58.5852 | 2.2678 | 0.20453
2025-02-07 13:13 | 0.79687 | 0.90464 | 26.3883 | 0.02264 | 0.97877 | 0.87547 | 0.001895 | 78160.9424 | 0.023694 | 1.6947 | 52.8237 | 61.4651 | 2.4046 | 0.21687
2025-02-07 13:14 | 0.70421 | 0.79945 | 26.3881 | 0.022745 | 0.97877 | 0.77367 | 0.0016746 | 69072.3787 | 0.023694 | 1.6947 | 47.4963 | 55.2659 | 2.1496 | 0.19386
2025-02-07 13:15 | 0.66715 | 0.75737 | 26.3879 | 0.022793 | 0.97877 | 0.73295 | 0.0015865 | 65436.9136 | 0.023694 | 1.6947 | 45.3384 | 52.7547 | 2.0468 | 0.18459
2025-02-07 13:16 | 0.80459 | 0.9134 | 26.3877 | 0.022841 | 0.97877 | 0.88396 | 0.0019133 | 78918.0402 | 0.023694 | 1.6947 | 53.2636 | 61.976 | 2.4481 | 0.22078
2025-02-07 13:17 | 0.8154 | 0.92567 | 26.3875 | 0.022889 | 0.97877 | 0.89583 | 0.001939 | 79978.2655 | 0.023695 | 1.6947 | 53.8785 | 62.6911 | 2.4843 | 0.22405
2025-02-07 13:18 | 0.8154 | 0.92567 | 26.3875 | 0.022964 | 0.97877 | 0.89583 | 0.001939 | 79978.2888 | 0.023695 | 1.6947 | 53.8785 | 62.6912 | 2.4925 | 0.22479
2025-02-07 13:19 | 0.78838 | 0.895 | 26.3879 | 0.022974 | 0.97877 | 0.86614 | 0.0018748 | 77327.6737 | 0.023694 | 1.6947 | 52.3392 | 60.9007 | 2.4155 | 0.21785
2025-02-07 13:20 | 0.77564 | 0.88053 | 26.3884 | 0.022899 | 0.97877 | 0.85214 | 0.0018445 | 76078.1864 | 0.023694 | 1.6947 | 51.6109 | 60.0539 | 2.3708 | 0.21382
2025-02-07 13:21 | 0.80305 | 0.91166 | 26.3888 | 0.022917 | 0.97877 | 0.88226 | 0.0019097 | 78767.0447 | 0.023694 | 1.6948 | 53.1757 | 61.8753 | 2.4518 | 0.22113
2025-02-07 13:22 | 0.80961 | 0.91911 | 26.3892 | 0.022955 | 0.97877 | 0.88947 | 0.0019253 | 79410.9986 | 0.023693 | 1.6948 | 53.5493 | 62.3106 | 2.4749 | 0.2232
2025-02-07 13:23 | 0.84552 | 0.95987 | 26.3898 | 0.022898 | 0.97877 | 0.92892 | 0.0020106 | 82933.0753 | 0.023693 | 1.6948 | 55.5854 | 64.6808 | 2.572 | 0.23196
2025-02-07 13:24 | 0.84436 | 0.95856 | 26.3907 | 0.022803 | 0.97876 | 0.92765 | 0.0020079 | 82819.855 | 0.023692 | 1.6948 | 55.5199 | 64.606 | 2.5581 | 0.23071
2025-02-07 13:25 | 0.81618 | 0.92657 | 26.3916 | 0.022793 | 0.97876 | 0.89668 | 0.0019409 | 80055.778 | 0.023692 | 1.6949 | 53.9224 | 62.7483 | 2.4764 | 0.22334
2025-02-07 13:26 | 0.82428 | 0.93578 | 26.3924 | 0.022869 | 0.97876 | 0.90559 | 0.0019601 | 80851.4093 | 0.023691 | 1.6949 | 54.3827 | 63.2852 | 2.508 | 0.22619
2025-02-07 13:27 | 0.81811 | 0.92877 | 26.3933 | 0.022908 | 0.97876 | 0.8988 | 0.0019455 | 80245.8699 | 0.02369 | 1.695 | 54.032 | 62.8784 | 2.4946 | 0.22498
2025-02-07 13:28 | 0.79649 | 0.90423 | 26.3936 | 0.023021 | 0.97876 | 0.87505 | 0.001894 | 78125.302 | 0.02369 | 1.695 | 52.8017 | 61.4472 | 2.4443 | 0.22045
2025-02-07 13:29 | 0.81154 | 0.92132 | 26.3932 | 0.02307 | 0.97876 | 0.89159 | 0.0019299 | 79602.038 | 0.023691 | 1.6949 | 53.659 | 62.4442 | 2.4932 | 0.22486
2025-02-07 13:30 | 0.79842 | 0.90642 | 26.3927 | 0.023136 | 0.97876 | 0.87717 | 0.0018986 | 78314.286 | 0.023691 | 1.6949 | 52.9118 | 61.574 | 2.4621 | 0.22205
2025-02-07 13:31 | 0.78374 | 0.88976 | 26.3923 | 0.023251 | 0.97876 | 0.86105 | 0.0018637 | 76875.063 | 0.023691 | 1.6949 | 52.0745 | 60.599 | 2.4313 | 0.21927
2025-02-07 13:32 | 0.78992 | 0.89677 | 26.3919 | 0.023318 | 0.97876 | 0.86784 | 0.0018784 | 77480.7934 | 0.023691 | 1.6949 | 52.4273 | 61.009 | 2.4564 | 0.22154
2025-02-07 13:33 | 0.80228 | 0.91079 | 26.3918 | 0.023366 | 0.97876 | 0.88141 | 0.0019078 | 78692.5654 | 0.023692 | 1.6949 | 53.1317 | 61.8285 | 2.4978 | 0.22527
2025-02-07 13:34 | 0.81038 | 0.92 | 26.3921 | 0.02347 | 0.97876 | 0.89032 | 0.0019271 | 79487.9554 | 0.023691 | 1.6949 | 53.5932 | 62.3659 | 2.5329 | 0.22843
2025-02-07 13:35 | 0.82158 | 0.93271 | 26.3924 | 0.023499 | 0.97876 | 0.90262 | 0.0019537 | 80586.3009 | 0.023691 | 1.6949 | 54.2293 | 63.1067 | 2.5691 | 0.2317
2025-02-07 13:36 | 0.81463 | 0.92482 | 26.3927 | 0.023509 | 0.97876 | 0.89498 | 0.0019372 | 79904.7853 | 0.023691 | 1.6949 | 53.8346 | 62.6478 | 2.5496 | 0.22995
2025-02-07 13:37 | 0.81424 | 0.92439 | 26.393 | 0.023584 | 0.97876 | 0.89456 | 0.0019363 | 79867.0485 | 0.023691 | 1.6949 | 53.8127 | 62.6227 | 2.5567 | 0.23059
2025-02-07 13:38 | 0.81579 | 0.92614 | 26.3933 | 0.023595 | 0.97876 | 0.89626 | 0.00194 | 80018.6571 | 0.02369 | 1.695 | 53.9004 | 62.7253 | 2.5625 | 0.2311
2025-02-07 13:39 | 0.80807 | 0.91738 | 26.3936 | 0.023604 | 0.97876 | 0.88777 | 0.0019216 | 79261.3945 | 0.02369 | 1.695 | 53.4614 | 62.2148 | 2.5406 | 0.22913
2025-02-07 13:40 | 0.72429 | 0.82226 | 26.3937 | 0.023623 | 0.97876 | 0.79573 | 0.0017224 | 71043.6893 | 0.02369 | 1.695 | 48.6585 | 56.6257 | 2.293 | 0.2068
2025-02-07 13:41 | 0.5965 | 0.67718 | 26.3935 | 0.023681 | 0.97876 | 0.65533 | 0.0014185 | 58508.7293 | 0.02369 | 1.695 | 41.1772 | 47.9192 | 1.9131 | 0.17254
2025-02-07 13:42 | 0.51387 | 0.58339 | 26.3932 | 0.023659 | 0.97876 | 0.56456 | 0.001222 | 50404.5495 | 0.02369 | 1.695 | 36.222 | 42.1524 | 1.6597 | 0.14969
2025-02-07 13:43 | 0.4772 | 0.54175 | 26.393 | 0.023564 | 0.97876 | 0.52427 | 0.0011348 | 46806.8755 | 0.023691 | 1.6949 | 33.9871 | 39.5515 | 1.541 | 0.13898
2025-02-07 13:44 | 0.42353 | 0.48082 | 26.3928 | 0.023498 | 0.97876 | 0.46531 | 0.0010072 | 41542.9471 | 0.023691 | 1.6949 | 30.673 | 35.6946 | 1.3722 | 0.12376
2025-02-07 13:45 | 0.38608 | 0.43831 | 26.3933 | 0.023421 | 0.97876 | 0.42416 | 0.0009181 | 37869.6855 | 0.02369 | 1.695 | 28.3256 | 32.9632 | 1.2526 | 0.11297
2025-02-07 13:46 | 0.38106 | 0.43261 | 26.3945 | 0.023295 | 0.97876 | 0.41865 | 0.00090617 | 37377.6398 | 0.02369 | 1.695 | 28.0086 | 32.5953 | 1.2306 | 0.11098
2025-02-07 13:47 | 0.38724 | 0.43963 | 26.3958 | 0.023065 | 0.97875 | 0.42544 | 0.00092086 | 37983.8228 | 0.023689 | 1.6951 | 28.3986 | 33.0502 | 1.2372 | 0.11158
2025-02-07 13:48 | 0.3884 | 0.44095 | 26.3971 | 0.022778 | 0.97875 | 0.42671 | 0.00092361 | 38097.7003 | 0.023688 | 1.6951 | 28.4717 | 33.1362 | 1.2254 | 0.11051
2025-02-07 13:49 | 0.40732 | 0.46243 | 26.3984 | 0.022435 | 0.97875 | 0.44749 | 0.0009686 | 39953.6314 | 0.023687 | 1.6952 | 29.6603 | 34.5207 | 1.2627 | 0.11388
2025-02-07 13:50 | 0.44747 | 0.50801 | 26.3993 | 0.022141 | 0.97875 | 0.49161 | 0.0010641 | 43892.4063 | 0.023686 | 1.6952 | 32.1581 | 37.4286 | 1.3625 | 0.12288
2025-02-07 13:51 | 0.4714 | 0.53519 | 26.3997 | 0.021962 | 0.97875 | 0.5179 | 0.001121 | 46240.512 | 0.023686 | 1.6952 | 33.6321 | 39.1446 | 1.4199 | 0.12806
2025-02-07 13:52 | 0.46137 | 0.5238 | 26.4002 | 0.021877 | 0.97874 | 0.50688 | 0.0010971 | 45255.9696 | 0.023686 | 1.6953 | 33.0153 | 38.427 | 1.3859 | 0.12499
2025-02-07 13:53 | 0.47411 | 0.53826 | 26.4006 | 0.021858 | 0.97874 | 0.52087 | 0.0011274 | 46505.8235 | 0.023685 | 1.6953 | 33.7979 | 39.3383 | 1.421 | 0.12815
2025-02-07 13:54 | 0.49766 | 0.565 | 26.401 | 0.021831 | 0.97874 | 0.54675 | 0.0011834 | 48816.0809 | 0.023685 | 1.6953 | 35.2368 | 41.0135 | 1.4859 | 0.13401
2025-02-07 13:55 | 0.48492 | 0.55054 | 26.4014 | 0.021957 | 0.97874 | 0.53275 | 0.0011531 | 47566.416 | 0.023685 | 1.6953 | 34.4596 | 40.1092 | 1.4583 | 0.13152
2025-02-07 13:56 | 0.47874 | 0.54352 | 26.4016 | 0.022107 | 0.97874 | 0.52596 | 0.0011384 | 46960.5291 | 0.023685 | 1.6953 | 34.0817 | 39.6696 | 1.4505 | 0.13082
2025-02-07 13:57 | 0.48299 | 0.54835 | 26.4018 | 0.022116 | 0.97874 | 0.53063 | 0.0011485 | 47377.1691 | 0.023684 | 1.6953 | 34.3416 | 39.9722 | 1.4633 | 0.13197
2025-02-07 13:58 | 0.46059 | 0.52292 | 26.402 | 0.022154 | 0.97874 | 0.50603 | 0.0010953 | 45180.6777 | 0.023684 | 1.6953 | 32.9678 | 38.3734 | 1.4013 | 0.12638
2025-02-07 13:59 | 0.45751 | 0.51942 | 26.4022 | 0.022049 | 0.97874 | 0.50263 | 0.001088 | 44877.7588 | 0.023684 | 1.6954 | 32.7776 | 38.1522 | 1.3858 | 0.12498
2025-02-07 14:00 | 0.43975 | 0.49926 | 26.4026 | 0.022219 | 0.97874 | 0.48312 | 0.0010457 | 43135.7634 | 0.023684 | 1.6954 | 31.6803 | 36.8753 | 1.345 | 0.1213
2025-02-07 14:01 | 0.41658 | 0.47296 | 26.4033 | 0.022352 | 0.97874 | 0.45767 | 0.00099063 | 40863.6093 | 0.023683 | 1.6954 | 30.2397 | 35.199 | 1.2854 | 0.11593
2025-02-07 14:02 | 0.40307 | 0.45762 | 26.4039 | 0.022275 | 0.97874 | 0.44283 | 0.0009585 | 39538.2361 | 0.023683 | 1.6954 | 29.3942 | 34.2154 | 1.2415 | 0.11197
2025-02-07 14:03 | 0.41465 | 0.47077 | 26.4046 | 0.022212 | 0.97874 | 0.45555 | 0.00098604 | 40674.5348 | 0.023682 | 1.6955 | 30.1191 | 35.0598 | 1.2717 | 0.1147
2025-02-07 14:04 | 0.42894 | 0.48699 | 26.4052 | 0.022344 | 0.97873 | 0.47125 | 0.00102 | 42075.946 | 0.023682 | 1.6955 | 31.0094 | 36.0966 | 1.3211 | 0.11915
2025-02-07 14:05 | 0.4243 | 0.48173 | 26.4059 | 0.022607 | 0.97873 | 0.46616 | 0.001009 | 41621.6256 | 0.023682 | 1.6955 | 30.7211 | 35.7616 | 1.323 | 0.11932
2025-02-07 14:06 | 0.40809 | 0.46332 | 26.4065 | 0.022537 | 0.97873 | 0.44834 | 0.00097043 | 40031.1299 | 0.023681 | 1.6955 | 29.7087 | 34.5836 | 1.271 | 0.11463
2025-02-07 14:07 | 0.3911 | 0.44404 | 26.4071 | 0.022341 | 0.97873 | 0.42968 | 0.00093004 | 38364.8767 | 0.023681 | 1.6956 | 28.642 | 33.3423 | 1.2101 | 0.10914
2025-02-07 14:08 | 0.42662 | 0.48437 | 26.4078 | 0.022259 | 0.97873 | 0.4687 | 0.0010145 | 41849.2965 | 0.02368 | 1.6956 | 30.8653 | 35.9311 | 1.3094 | 0.1181
2025-02-07 14:09 | 0.46098 | 0.52338 | 26.4084 | 0.022329 | 0.97873 | 0.50645 | 0.0010962 | 45220.1222 | 0.02368 | 1.6956 | 32.9915 | 38.4069 | 1.4138 | 0.12751
2025-02-07 14:10 | 0.45249 | 0.51374 | 26.409 | 0.022383 | 0.97873 | 0.49712 | 0.001076 | 44387.0564 | 0.023679 | 1.6957 | 32.4681 | 37.798 | 1.3924 | 0.12558
2025-02-07 14:11 | 0.45558 | 0.51725 | 26.4095 | 0.022386 | 0.97873 | 0.50051 | 0.0010834 | 44690.151 | 0.023679 | 1.6957 | 32.6586 | 38.0202 | 1.4016 | 0.12641
2025-02-07 14:12 | 0.45828 | 0.52032 | 26.4099 | 0.022591 | 0.97872 | 0.50348 | 0.0010898 | 44955.3749 | 0.023679 | 1.6957 | 32.8251 | 38.2145 | 1.4225 | 0.12829
2025-02-07 14:13 | 0.46368 | 0.52645 | 26.4104 | 0.022687 | 0.97872 | 0.50942 | 0.0011026 | 45485.7118 | 0.023678 | 1.6957 | 33.1578 | 38.6022 | 1.4445 | 0.13027
2025-02-07 14:14 | 0.43897 | 0.4984 | 26.4108 | 0.022668 | 0.97872 | 0.48227 | 0.0010439 | 43061.9347 | 0.023678 | 1.6957 | 31.6324 | 36.8268 | 1.3702 | 0.12358
2025-02-07 14:15 | 0.44631 | 0.50673 | 26.4113 | 0.022552 | 0.97872 | 0.49033 | 0.0010613 | 43781.6364 | 0.023678 | 1.6958 | 32.0865 | 37.3558 | 1.3848 | 0.12489
2025-02-07 14:16 | 0.466 | 0.52909 | 26.4118 | 0.022598 | 0.97872 | 0.51197 | 0.0011081 | 45713.2931 | 0.023677 | 1.6958 | 33.3002 | 38.7693 | 1.4457 | 0.13039
2025-02-07 14:17 | 0.44785 | 0.50849 | 26.4117 | 0.022728 | 0.97872 | 0.49203 | 0.001065 | 43933.2251 | 0.023677 | 1.6958 | 32.182 | 37.4673 | 1.4002 | 0.12628
2025-02-07 14:18 | 0.41851 | 0.47517 | 26.4111 | 0.022675 | 0.97872 | 0.45979 | 0.00099522 | 41054.6984 | 0.023678 | 1.6957 | 30.3602 | 35.3458 | 1.3099 | 0.11814
2025-02-07 14:19 | 0.42121 | 0.47824 | 26.4104 | 0.022652 | 0.97872 | 0.46276 | 0.0010016 | 41319.6684 | 0.023678 | 1.6957 | 30.5287 | 35.5414 | 1.3166 | 0.11874
2025-02-07 14:20 | 0.43627 | 0.49533 | 26.4098 | 0.022673 | 0.97872 | 0.4793 | 0.0010375 | 42796.5741 | 0.023679 | 1.6957 | 31.4649 | 36.6308 | 1.3625 | 0.12288
2025-02-07 14:21 | 0.42894 | 0.487 | 26.4091 | 0.02288 | 0.97873 | 0.47125 | 0.00102 | 42076.8388 | 0.023679 | 1.6957 | 31.0094 | 36.1 | 1.3529 | 0.12202
2025-02-07 14:22 | 0.43396 | 0.4927 | 26.4093 | 0.022849 | 0.97873 | 0.47676 | 0.0010319 | 42569.2234 | 0.023679 | 1.6957 | 31.3212 | 36.4631 | 1.3661 | 0.12321
2025-02-07 14:23 | 0.45056 | 0.51155 | 26.4104 | 0.022674 | 0.97872 | 0.495 | 0.0010714 | 44198.0182 | 0.023678 | 1.6957 | 32.3489 | 37.6605 | 1.4048 | 0.1267
2025-02-07 14:24 | 0.45094 | 0.51199 | 26.4114 | 0.022654 | 0.97872 | 0.49542 | 0.0010723 | 44236.1471 | 0.023678 | 1.6958 | 32.3727 | 37.6892 | 1.4048 | 0.1267
2025-02-07 14:25 | 0.44785 | 0.50849 | 26.4125 | 0.022793 | 0.97872 | 0.49203 | 0.001065 | 43933.4154 | 0.023677 | 1.6958 | 32.182 | 37.4681 | 1.4043 | 0.12665
2025-02-07 14:26 | 0.44515 | 0.50542 | 26.4136 | 0.022979 | 0.97872 | 0.48906 | 0.0010586 | 43668.5531 | 0.023676 | 1.6959 | 32.0149 | 37.2745 | 1.4077 | 0.12696
2025-02-07 14:27 | 0.43202 | 0.49052 | 26.415 | 0.022897 | 0.97871 | 0.47464 | 0.0010274 | 42381.1582 | 0.023675 | 1.6959 | 31.2013 | 36.3284 | 1.3634 | 0.12296
2025-02-07 14:28 | 0.43627 | 0.49535 | 26.4167 | 0.022721 | 0.97871 | 0.4793 | 0.0010375 | 42798.1726 | 0.023674 | 1.696 | 31.4649 | 36.6368 | 1.3656 | 0.12316
2025-02-07 14:29 | 0.41928 | 0.47607 | 26.4184 | 0.02267 | 0.97871 | 0.46064 | 0.00099706 | 41132.0774 | 0.023673 | 1.6961 | 30.4083 | 35.408 | 1.3122 | 0.11835
2025-02-07 14:30 | 0.39921 | 0.45327 | 26.4201 | 0.0227 | 0.9787 | 0.43858 | 0.00094932 | 39162.9493 | 0.023671 | 1.6962 | 29.1519 | 33.9464 | 1.2543 | 0.11312
2025-02-07 14:31 | 0.40925 | 0.46468 | 26.4218 | 0.022751 | 0.9787 | 0.44961 | 0.00097319 | 40148.0786 | 0.02367 | 1.6962 | 29.7812 | 34.6806 | 1.2871 | 0.11608
2025-02-07 14:32 | 0.43087 | 0.48923 | 26.4229 | 0.022945 | 0.9787 | 0.47337 | 0.0010246 | 42269.3522 | 0.02367 | 1.6963 | 31.1293 | 36.2514 | 1.3631 | 0.12294
2025-02-07 14:33 | 0.44052 | 0.50019 | 26.4232 | 0.02293 | 0.9787 | 0.48397 | 0.0010476 | 43216.3182 | 0.023669 | 1.6963 | 31.7281 | 36.949 | 1.3912 | 0.12547
2025-02-07 14:34 | 0.4521 | 0.51334 | 26.4235 | 0.022921 | 0.9787 | 0.4967 | 0.0010751 | 44352.6661 | 0.023669 | 1.6963 | 32.4442 | 37.7833 | 1.4253 | 0.12855
2025-02-07 14:35 | 0.42044 | 0.47739 | 26.4238 | 0.022985 | 0.9787 | 0.46191 | 0.00099981 | 41246.9109 | 0.023669 | 1.6963 | 30.4805 | 35.4967 | 1.3342 | 0.12033
2025-02-07 14:36 | 0.40693 | 0.46205 | 26.4241 | 0.022973 | 0.9787 | 0.44707 | 0.00096768 | 39921.3201 | 0.023669 | 1.6963 | 29.6361 | 34.5136 | 1.2927 | 0.11659
2025-02-07 14:37 | 0.45056 | 0.51159 | 26.4244 | 0.022987 | 0.97869 | 0.495 | 0.0010714 | 44201.3835 | 0.023668 | 1.6963 | 32.3489 | 37.6731 | 1.4248 | 0.1285
2025-02-07 14:38 | 0.46059 | 0.52299 | 26.4247 | 0.023031 | 0.97869 | 0.50603 | 0.0010953 | 45186.2355 | 0.023668 | 1.6964 | 32.9678 | 38.394 | 1.4577 | 0.13147
2025-02-07 14:39 | 0.4633 | 0.52606 | 26.4249 | 0.022899 | 0.97869 | 0.509 | 0.0011017 | 45451.4086 | 0.023668 | 1.6964 | 33.1341 | 38.5879 | 1.4574 | 0.13144
2025-02-07 14:40 | 0.47102 | 0.53483 | 26.4249 | 0.022995 | 0.97869 | 0.51748 | 0.0011201 | 46208.9313 | 0.023668 | 1.6964 | 33.6084 | 39.1403 | 1.4867 | 0.13408
2025-02-07 14:41 | 0.47411 | 0.53833 | 26.4249 | 0.022912 | 0.97869 | 0.52087 | 0.0011274 | 46511.9404 | 0.023668 | 1.6964 | 33.7979 | 39.3609 | 1.4905 | 0.13443
2025-02-07 14:42 | 0.45751 | 0.51948 | 26.4249 | 0.022843 | 0.97869 | 0.50263 | 0.001088 | 44883.2656 | 0.023668 | 1.6964 | 32.7776 | 38.1727 | 1.4366 | 0.12956
2025-02-07 14:43 | 0.46291 | 0.52562 | 26.4249 | 0.022834 | 0.97869 | 0.50857 | 0.0011008 | 45413.5312 | 0.023668 | 1.6964 | 33.1103 | 38.5602 | 1.4522 | 0.13097
2025-02-07 14:44 | 0.47411 | 0.53833 | 26.4249 | 0.02306 | 0.97869 | 0.52087 | 0.0011274 | 46511.9404 | 0.023668 | 1.6964 | 33.7979 | 39.3609 | 1.5001 | 0.13529
2025-02-07 14:45 | 0.47681 | 0.5414 | 26.4249 | 0.023131 | 0.97869 | 0.52384 | 0.0011339 | 46777.0743 | 0.023668 | 1.6964 | 33.9635 | 39.5538 | 1.5129 | 0.13645
2025-02-07 14:46 | 0.49187 | 0.5585 | 26.4255 | 0.023096 | 0.97869 | 0.54038 | 0.0011697 | 48254.4076 | 0.023668 | 1.6964 | 34.8839 | 40.6263 | 1.5558 | 0.14032
2025-02-07 14:47 | 0.48453 | 0.55017 | 26.4268 | 0.023006 | 0.97869 | 0.53233 | 0.0011522 | 47535.0893 | 0.023667 | 1.6965 | 34.436 | 40.1059 | 1.5279 | 0.13779
2025-02-07 14:48 | 0.49341 | 0.56026 | 26.4281 | 0.022985 | 0.97869 | 0.54208 | 0.0011733 | 48406.5878 | 0.023666 | 1.6965 | 34.978 | 40.7384 | 1.5531 | 0.14007
2025-02-07 14:49 | 0.5077 | 0.57649 | 26.4294 | 0.022943 | 0.97868 | 0.55777 | 0.0012073 | 49808.3783 | 0.023665 | 1.6966 | 35.8472 | 41.752 | 1.5928 | 0.14365
2025-02-07 14:50 | 0.51465 | 0.58438 | 26.4307 | 0.023033 | 0.97868 | 0.56541 | 0.0012238 | 50490.5172 | 0.023664 | 1.6966 | 36.2688 | 42.2443 | 1.6198 | 0.14609
2025-02-07 14:51 | 0.52623 | 0.59754 | 26.4315 | 0.023131 | 0.97868 | 0.57813 | 0.0012514 | 51627.0834 | 0.023663 | 1.6967 | 36.9696 | 43.0615 | 1.6614 | 0.14984
2025-02-07 14:52 | 0.51773 | 0.58789 | 26.432 | 0.023207 | 0.97868 | 0.5688 | 0.0012312 | 50793.8973 | 0.023663 | 1.6967 | 36.4559 | 42.4636 | 1.6414 | 0.14803
2025-02-07 14:53 | 0.50384 | 0.57211 | 26.4324 | 0.023175 | 0.97868 | 0.55353 | 0.0011981 | 49430.4172 | 0.023663 | 1.6967 | 35.6126 | 41.4818 | 1.5974 | 0.14407
2025-02-07 14:54 | 0.49573 | 0.56291 | 26.4328 | 0.022961 | 0.97868 | 0.54463 | 0.0011788 | 48635.0982 | 0.023663 | 1.6967 | 35.1192 | 40.9074 | 1.5586 | 0.14056
2025-02-07 14:55 | 0.48801 | 0.55414 | 26.4332 | 0.022952 | 0.97868 | 0.53614 | 0.0011605 | 47877.6546 | 0.023662 | 1.6967 | 34.6482 | 40.3593 | 1.535 | 0.13843
2025-02-07 14:56 | 0.46947 | 0.5331 | 26.4337 | 0.022942 | 0.97868 | 0.51578 | 0.0011164 | 46059.623 | 0.023662 | 1.6968 | 33.5136 | 39.0381 | 1.479 | 0.13339
2025-02-07 14:57 | 0.47604 | 0.54055 | 26.4341 | 0.022973 | 0.97868 | 0.52299 | 0.001132 | 46703.6569 | 0.023662 | 1.6968 | 33.9162 | 39.5074 | 1.5007 | 0.13534
2025-02-07 14:58 | 0.49843 | 0.56598 | 26.4345 | 0.023103 | 0.97867 | 0.54759 | 0.0011853 | 48900.6993 | 0.023661 | 1.6968 | 35.2838 | 41.1008 | 1.5764 | 0.14217
2025-02-07 14:59 | 0.48994 | 0.55634 | 26.435 | 0.023331 | 0.97867 | 0.53826 | 0.0011651 | 48067.4903 | 0.023661 | 1.6968 | 34.7661 | 40.4982 | 1.5662 | 0.14126
2025-02-07 15:00 | 0.4799 | 0.54494 | 26.4354 | 0.023209 | 0.97867 | 0.52724 | 0.0011412 | 47082.7661 | 0.023661 | 1.6968 | 34.1526 | 39.784 | 1.5278 | 0.13779
2025-02-07 15:01 | 0.48106 | 0.54626 | 26.4358 | 0.023073 | 0.97867 | 0.52851 | 0.001144 | 47196.4963 | 0.02366 | 1.6969 | 34.2235 | 39.8669 | 1.5223 | 0.13729
2025-02-07 15:02 | 0.47681 | 0.54143 | 26.4361 | 0.023303 | 0.97867 | 0.52384 | 0.0011339 | 46779.9111 | 0.02366 | 1.6969 | 33.9635 | 39.5643 | 1.5247 | 0.13751
2025-02-07 15:03 | 0.47102 | 0.53486 | 26.4364 | 0.023365 | 0.97867 | 0.51748 | 0.0011201 | 46211.8101 | 0.02366 | 1.6969 | 33.6084 | 39.151 | 1.5111 | 0.13628
2025-02-07 15:04 | 0.48376 | 0.54933 | 26.4367 | 0.023182 | 0.97867 | 0.53148 | 0.0011504 | 47461.8802 | 0.02366 | 1.6969 | 34.3888 | 40.0603 | 1.5377 | 0.13868
2025-02-07 15:05 | 0.4826 | 0.54801 | 26.437 | 0.023257 | 0.97867 | 0.5302 | 0.0011476 | 47348.3245 | 0.02366 | 1.6969 | 34.318 | 39.9781 | 1.5392 | 0.13882
2025-02-07 15:06 | 0.48106 | 0.54626 | 26.4373 | 0.023342 | 0.97867 | 0.52851 | 0.001144 | 47196.8884 | 0.023659 | 1.6969 | 34.2235 | 39.8683 | 1.5401 | 0.1389
2025-02-07 15:07 | 0.47874 | 0.54363 | 26.4376 | 0.023522 | 0.97867 | 0.52596 | 0.0011384 | 46969.6943 | 0.023659 | 1.6969 | 34.0817 | 39.7035 | 1.5449 | 0.13933
2025-02-07 15:08 | 0.46021 | 0.52259 | 26.4381 | 0.023401 | 0.97867 | 0.5056 | 0.0010944 | 45151.6291 | 0.023659 | 1.697 | 32.944 | 38.3785 | 1.4805 | 0.13353
2025-02-07 15:09 | 0.46098 | 0.52347 | 26.4387 | 0.023319 | 0.97867 | 0.50645 | 0.0010962 | 45227.5445 | 0.023658 | 1.697 | 32.9915 | 38.4345 | 1.4777 | 0.13327
2025-02-07 15:10 | 0.46947 | 0.53311 | 26.4394 | 0.023245 | 0.97866 | 0.51578 | 0.0011164 | 46061.044 | 0.023658 | 1.697 | 33.5136 | 39.0433 | 1.4988 | 0.13517
2025-02-07 15:11 | 0.45866 | 0.52084 | 26.44 | 0.023349 | 0.97866 | 0.50391 | 0.0010907 | 45000.584 | 0.023657 | 1.6971 | 32.8489 | 38.2695 | 1.4726 | 0.13281
2025-02-07 15:12 | 0.46059 | 0.52303 | 26.4407 | 0.023272 | 0.97866 | 0.50603 | 0.0010953 | 45190.1393 | 0.023657 | 1.6971 | 32.9678 | 38.4086 | 1.4736 | 0.1329
2025-02-07 15:13 | 0.47295 | 0.53707 | 26.4413 | 0.023133 | 0.97866 | 0.5196 | 0.0011247 | 46402.4437 | 0.023657 | 1.6971 | 33.7269 | 39.2935 | 1.5021 | 0.13547
2025-02-07 15:14 | 0.48453 | 0.55022 | 26.442 | 0.023198 | 0.97866 | 0.53233 | 0.0011522 | 47538.9952 | 0.023656 | 1.6971 | 34.436 | 40.1203 | 1.5413 | 0.13901
2025-02-07 15:15 | 0.47218 | 0.53619 | 26.4426 | 0.023403 | 0.97866 | 0.51875 | 0.0011228 | 46327.0061 | 0.023656 | 1.6972 | 33.6795 | 39.2395 | 1.5174 | 0.13685
2025-02-07 15:16 | 0.47025 | 0.534 | 26.4432 | 0.023501 | 0.97866 | 0.51663 | 0.0011182 | 46137.7687 | 0.023655 | 1.6972 | 33.561 | 39.1021 | 1.5178 | 0.13689
2025-02-07 15:17 | 0.48839 | 0.55461 | 26.4439 | 0.023146 | 0.97866 | 0.53657 | 0.0011614 | 47918.2949 | 0.023655 | 1.6972 | 34.6718 | 40.3969 | 1.5495 | 0.13975
2025-02-07 15:18 | 0.49303 | 0.55987 | 26.4441 | 0.023216 | 0.97865 | 0.54166 | 0.0011724 | 48372.9083 | 0.023655 | 1.6972 | 34.9545 | 40.7265 | 1.5682 | 0.14143
2025-02-07 15:19 | 0.48608 | 0.55198 | 26.4439 | 0.023368 | 0.97866 | 0.53402 | 0.0011559 | 47691.0092 | 0.023655 | 1.6972 | 34.5303 | 40.2321 | 1.5574 | 0.14046
2025-02-07 15:20 | 0.47449 | 0.53883 | 26.4437 | 0.023347 | 0.97866 | 0.5213 | 0.0011283 | 46554.5537 | 0.023655 | 1.6972 | 33.8215 | 39.406 | 1.5208 | 0.13716
2025-02-07 15:21 | 0.46368 | 0.52655 | 26.4434 | 0.02318 | 0.97866 | 0.50942 | 0.0011026 | 45493.8614 | 0.023655 | 1.6972 | 33.1578 | 38.6325 | 1.4773 | 0.13323
2025-02-07 15:22 | 0.45056 | 0.51164 | 26.4432 | 0.023297 | 0.97866 | 0.495 | 0.0010714 | 44205.8897 | 0.023655 | 1.6972 | 32.3489 | 37.6899 | 1.4448 | 0.1303
2025-02-07 15:23 | 0.46446 | 0.52742 | 26.4429 | 0.023506 | 0.97866 | 0.51027 | 0.0011045 | 45569.4814 | 0.023655 | 1.6972 | 33.2053 | 38.6873 | 1.5004 | 0.13532
2025-02-07 15:24 | 0.48222 | 0.54759 | 26.4424 | 0.023285 | 0.97866 | 0.52978 | 0.0011467 | 47311.8377 | 0.023656 | 1.6972 | 34.2943 | 39.9557 | 1.5401 | 0.1389
2025-02-07 15:25 | 0.49766 | 0.56513 | 26.442 | 0.023214 | 0.97866 | 0.54675 | 0.0011834 | 48826.9074 | 0.023656 | 1.6971 | 35.2368 | 41.0533 | 1.5819 | 0.14267
2025-02-07 15:26 | 0.49843 | 0.566 | 26.4415 | 0.023342 | 0.97866 | 0.54759 | 0.0011853 | 48902.5448 | 0.023656 | 1.6971 | 35.2838 | 41.1076 | 1.593 | 0.14367
2025-02-07 15:27 | 0.49187 | 0.55855 | 26.441 | 0.023478 | 0.97866 | 0.54038 | 0.0011697 | 48258.4706 | 0.023657 | 1.6971 | 34.8839 | 40.6412 | 1.5823 | 0.1427
2025-02-07 15:28 | 0.48646 | 0.55241 | 26.4406 | 0.023398 | 0.97866 | 0.53445 | 0.0011568 | 47728.039 | 0.023657 | 1.6971 | 34.5539 | 40.2564 | 1.5604 | 0.14073
2025-02-07 15:29 | 0.49611 | 0.56337 | 26.4401 | 0.023337 | 0.97866 | 0.54505 | 0.0011798 | 48674.9022 | 0.023657 | 1.6971 | 35.1427 | 40.9419 | 1.5856 | 0.143
2025-02-07 15:30 | 0.50384 | 0.57214 | 26.4402 | 0.023338 | 0.97866 | 0.55353 | 0.0011981 | 49432.5223 | 0.023657 | 1.6971 | 35.6126 | 41.4895 | 1.609 | 0.14511
2025-02-07 15:31 | 0.49573 | 0.56293 | 26.4409 | 0.023365 | 0.97866 | 0.54463 | 0.0011788 | 48637.2256 | 0.023657 | 1.6971 | 35.1192 | 40.9153 | 1.5864 | 0.14307
2025-02-07 15:32 | 0.48608 | 0.55197 | 26.4415 | 0.023252 | 0.97866 | 0.53402 | 0.0011559 | 47690.4056 | 0.023656 | 1.6971 | 34.5303 | 40.2298 | 1.5495 | 0.13975
2025-02-07 15:33 | 0.46098 | 0.52348 | 26.4422 | 0.023161 | 0.97866 | 0.50645 | 0.0010962 | 45228.391 | 0.023656 | 1.6971 | 32.9915 | 38.4376 | 1.4678 | 0.13238
2025-02-07 15:34 | 0.45635 | 0.51822 | 26.4428 | 0.023146 | 0.97866 | 0.50136 | 0.0010852 | 44773.9911 | 0.023655 | 1.6972 | 32.7062 | 38.1058 | 1.4529 | 0.13104
2025-02-07 15:35 | 0.46677 | 0.53006 | 26.4433 | 0.023151 | 0.97866 | 0.51281 | 0.00111 | 45796.8605 | 0.023655 | 1.6972 | 33.3477 | 38.8536 | 1.4848 | 0.13391
2025-02-07 15:36 | 0.45866 | 0.52085 | 26.4436 | 0.023305 | 0.97866 | 0.50391 | 0.0010907 | 45001.4558 | 0.023655 | 1.6972 | 32.8489 | 38.2727 | 1.47 | 0.13258
2025-02-07 15:37 | 0.45866 | 0.52085 | 26.4439 | 0.023185 | 0.97866 | 0.50391 | 0.0010907 | 45001.5306 | 0.023655 | 1.6972 | 32.8489 | 38.273 | 1.4624 | 0.13189
2025-02-07 15:38 | 0.46059 | 0.52304 | 26.4442 | 0.023069 | 0.97865 | 0.50603 | 0.0010953 | 45191.0068 | 0.023655 | 1.6972 | 32.9678 | 38.4118 | 1.461 | 0.13176
2025-02-07 15:39 | 0.4633 | 0.52611 | 26.4445 | 0.023178 | 0.97865 | 0.509 | 0.0011017 | 45456.2443 | 0.023654 | 1.6973 | 33.1341 | 38.6058 | 1.476 | 0.13312
2025-02-07 15:40 | 0.4382 | 0.49762 | 26.4448 | 0.023075 | 0.97865 | 0.48143 | 0.001042 | 42994.1021 | 0.023654 | 1.6973 | 31.5846 | 36.8007 | 1.3939 | 0.12571
2025-02-07 15:41 | 0.40886 | 0.4643 | 26.4451 | 0.022975 | 0.97865 | 0.44919 | 0.00097227 | 40115.2684 | 0.023654 | 1.6973 | 29.757 | 34.6716 | 1.2995 | 0.1172
2025-02-07 15:42 | 0.43434 | 0.49323 | 26.4456 | 0.023119 | 0.97865 | 0.47718 | 0.0010329 | 42615.4823 | 0.023654 | 1.6973 | 31.3451 | 36.5224 | 1.3849 | 0.1249
2025-02-07 15:43 | 0.46059 | 0.52305 | 26.4463 | 0.023126 | 0.97865 | 0.50603 | 0.0010953 | 45191.5088 | 0.023653 | 1.6973 | 32.9678 | 38.4137 | 1.4647 | 0.1321
2025-02-07 15:44 | 0.45365 | 0.51516 | 26.4469 | 0.023067 | 0.97865 | 0.49839 | 0.0010788 | 44509.815 | 0.023653 | 1.6974 | 32.5395 | 37.9153 | 1.44 | 0.12987
2025-02-07 15:45 | 0.44399 | 0.5042 | 26.4475 | 0.023113 | 0.97865 | 0.48779 | 0.0010558 | 43562.9493 | 0.023652 | 1.6974 | 31.9432 | 37.221 | 1.4138 | 0.1275
2025-02-07 15:46 | 0.44168 | 0.50157 | 26.4482 | 0.023021 | 0.97865 | 0.48524 | 0.0010503 | 43335.8157 | 0.023652 | 1.6974 | 31.7999 | 37.0545 | 1.4012 | 0.12637
2025-02-07 15:47 | 0.42508 | 0.48272 | 26.4486 | 0.023183 | 0.97865 | 0.467 | 0.0010108 | 41707.0401 | 0.023651 | 1.6974 | 30.7692 | 35.8539 | 1.3607 | 0.12272
2025-02-07 15:48 | 0.42083 | 0.4779 | 26.449 | 0.023156 | 0.97864 | 0.46234 | 0.0010007 | 41290.4164 | 0.023651 | 1.6975 | 30.5046 | 35.5459 | 1.3462 | 0.12141
2025-02-07 15:49 | 0.44747 | 0.50815 | 26.4493 | 0.023069 | 0.97864 | 0.49161 | 0.0010641 | 43904.2868 | 0.023651 | 1.6975 | 32.1581 | 37.4729 | 1.4217 | 0.12822
2025-02-07 15:50 | 0.47527 | 0.53972 | 26.4496 | 0.023185 | 0.97864 | 0.52215 | 0.0011302 | 46631.8097 | 0.023651 | 1.6975 | 33.8689 | 39.4667 | 1.5129 | 0.13644
2025-02-07 15:51 | 0.47449 | 0.53884 | 26.4499 | 0.023311 | 0.97864 | 0.5213 | 0.0011283 | 46556.1245 | 0.023651 | 1.6975 | 33.8215 | 39.4118 | 1.5187 | 0.13697
2025-02-07 15:52 | 0.4714 | 0.53534 | 26.4502 | 0.023403 | 0.97864 | 0.5179 | 0.001121 | 46253.1517 | 0.02365 | 1.6975 | 33.6321 | 39.1914 | 1.5153 | 0.13666
2025-02-07 15:53 | 0.47295 | 0.53709 | 26.4505 | 0.023397 | 0.97864 | 0.5196 | 0.0011247 | 46404.754 | 0.02365 | 1.6975 | 33.7269 | 39.3021 | 1.5197 | 0.13706
2025-02-07 15:54 | 0.48453 | 0.55025 | 26.4506 | 0.023351 | 0.97864 | 0.53233 | 0.0011522 | 47541.2319 | 0.02365 | 1.6975 | 34.436 | 40.1286 | 1.5518 | 0.13996
2025-02-07 15:55 | 0.46639 | 0.52964 | 26.4506 | 0.023343 | 0.97864 | 0.51239 | 0.0011091 | 45760.8037 | 0.02365 | 1.6975 | 33.3239 | 38.8327 | 1.4962 | 0.13494
2025-02-07 15:56 | 0.4467 | 0.50728 | 26.4506 | 0.023504 | 0.97864 | 0.49076 | 0.0010622 | 43828.8502 | 0.02365 | 1.6975 | 32.1104 | 37.4185 | 1.4462 | 0.13043
2025-02-07 15:57 | 0.45712 | 0.51912 | 26.4506 | 0.023545 | 0.97864 | 0.50221 | 0.001087 | 44851.6491 | 0.02365 | 1.6975 | 32.7538 | 38.1683 | 1.4807 | 0.13354
2025-02-07 15:58 | 0.466 | 0.5292 | 26.4506 | 0.02363 | 0.97864 | 0.51197 | 0.0011081 | 45722.9235 | 0.02365 | 1.6975 | 33.3002 | 38.805 | 1.5134 | 0.13649
2025-02-07 15:59 | 0.45751 | 0.51955 | 26.4506 | 0.023696 | 0.97864 | 0.50263 | 0.001088 | 44889.53 | 0.02365 | 1.6975 | 32.7776 | 38.196 | 1.4914 | 0.1345
2025-02-07 16:00 | 0.45519 | 0.51692 | 26.4506 | 0.023481 | 0.97864 | 0.50009 | 0.0010824 | 44662.2411 | 0.02365 | 1.6975 | 32.6348 | 38.0296 | 1.4707 | 0.13264
2025-02-07 16:01 | 0.46909 | 0.53271 | 26.4509 | 0.023352 | 0.97864 | 0.51536 | 0.0011155 | 46026.0335 | 0.02365 | 1.6975 | 33.4899 | 39.0264 | 1.505 | 0.13573
2025-02-07 16:02 | 0.47913 | 0.54411 | 26.4513 | 0.023379 | 0.97864 | 0.52639 | 0.0011394 | 47011.0615 | 0.02365 | 1.6976 | 34.1053 | 39.7439 | 1.5373 | 0.13865
2025-02-07 16:03 | 0.47411 | 0.53841 | 26.4517 | 0.023615 | 0.97864 | 0.52087 | 0.0011274 | 46518.7082 | 0.023649 | 1.6976 | 33.7979 | 39.386 | 1.5374 | 0.13866
2025-02-07 16:04 | 0.44978 | 0.51079 | 26.4522 | 0.023546 | 0.97864 | 0.49415 | 0.0010696 | 44132.2661 | 0.023649 | 1.6976 | 32.3012 | 37.6423 | 1.4583 | 0.13152
2025-02-07 16:05 | 0.43666 | 0.49588 | 26.4526 | 0.023382 | 0.97864 | 0.47973 | 0.0010384 | 42844.3863 | 0.023649 | 1.6976 | 31.4888 | 36.6959 | 1.408 | 0.12699
2025-02-07 16:06 | 0.43897 | 0.49852 | 26.4529 | 0.023439 | 0.97864 | 0.48227 | 0.0010439 | 43071.7504 | 0.023648 | 1.6976 | 31.6324 | 36.8636 | 1.4186 | 0.12794
2025-02-07 16:07 | 0.43087 | 0.48931 | 26.4531 | 0.023509 | 0.97864 | 0.47337 | 0.0010246 | 42276.2789 | 0.023648 | 1.6976 | 31.1293 | 36.2774 | 1.3979 | 0.12607
2025-02-07 16:08 | 0.44438 | 0.50466 | 26.4533 | 0.023401 | 0.97864 | 0.48821 | 0.0010567 | 43602.1984 | 0.023648 | 1.6976 | 31.9671 | 37.254 | 1.4328 | 0.12922
2025-02-07 16:09 | 0.46137 | 0.52395 | 26.4535 | 0.023567 | 0.97864 | 0.50688 | 0.0010971 | 45269.0586 | 0.023648 | 1.6977 | 33.0153 | 38.4757 | 1.4953 | 0.13486
2025-02-07 16:10 | 0.45673 | 0.51869 | 26.4538 | 0.023505 | 0.97864 | 0.50179 | 0.0010861 | 44814.5264 | 0.023648 | 1.6977 | 32.73 | 38.1434 | 1.4772 | 0.13322
2025-02-07 16:11 | 0.4521 | 0.51343 | 26.454 | 0.023537 | 0.97863 | 0.4967 | 0.0010751 | 44359.9936 | 0.023648 | 1.6977 | 32.4442 | 37.8106 | 1.4649 | 0.13212
2025-02-07 16:12 | 0.4494 | 0.51036 | 26.4542 | 0.023644 | 0.97863 | 0.49373 | 0.0010687 | 44094.8688 | 0.023647 | 1.6977 | 32.2774 | 37.6163 | 1.4632 | 0.13197
2025-02-07 16:13 | 0.44747 | 0.50817 | 26.4544 | 0.023667 | 0.97863 | 0.49161 | 0.0010641 | 43905.51 | 0.023647 | 1.6977 | 32.1581 | 37.4775 | 1.4587 | 0.13155
2025-02-07 16:14 | 0.44283 | 0.5029 | 26.4546 | 0.023577 | 0.97863 | 0.48652 | 0.0010531 | 43450.9745 | 0.023647 | 1.6977 | 31.8716 | 37.1437 | 1.4389 | 0.12977
2025-02-07 16:15 | 0.43241 | 0.49107 | 26.4548 | 0.023762 | 0.97863 | 0.47506 | 0.0010283 | 42428.202 | 0.023647 | 1.6977 | 31.2253 | 36.3907 | 1.4178 | 0.12787
2025-02-07 16:16 | 0.42353 | 0.48098 | 26.4554 | 0.02368 | 0.97863 | 0.46531 | 0.0010072 | 41557.039 | 0.023647 | 1.6977 | 30.673 | 35.7476 | 1.3854 | 0.12494
2025-02-07 16:17 | 0.42816 | 0.48625 | 26.4563 | 0.023383 | 0.97863 | 0.4704 | 0.0010182 | 42011.823 | 0.023646 | 1.6978 | 30.9613 | 36.0844 | 1.3822 | 0.12466
2025-02-07 16:18 | 0.43087 | 0.48932 | 26.4571 | 0.023329 | 0.97863 | 0.47337 | 0.0010246 | 42277.1991 | 0.023645 | 1.6978 | 31.1293 | 36.2809 | 1.3873 | 0.12512
2025-02-07 16:19 | 0.43859 | 0.49809 | 26.458 | 0.023471 | 0.97863 | 0.48185 | 0.001043 | 43035.0545 | 0.023645 | 1.6979 | 31.6085 | 36.8401 | 1.4195 | 0.12802
2025-02-07 16:20 | 0.44361 | 0.50379 | 26.4588 | 0.023428 | 0.97862 | 0.48736 | 0.0010549 | 43527.7343 | 0.023644 | 1.6979 | 31.9193 | 37.2032 | 1.4323 | 0.12918
2025-02-07 16:21 | 0.44515 | 0.50555 | 26.4591 | 0.023484 | 0.97862 | 0.48906 | 0.0010586 | 43679.3257 | 0.023644 | 1.6979 | 32.0149 | 37.3147 | 1.4405 | 0.12992
2025-02-07 16:22 | 0.46446 | 0.52747 | 26.4589 | 0.023428 | 0.97862 | 0.51027 | 0.0011045 | 45573.433 | 0.023644 | 1.6979 | 33.2053 | 38.702 | 1.4961 | 0.13493
2025-02-07 16:23 | 0.46291 | 0.52572 | 26.4587 | 0.023485 | 0.97863 | 0.50857 | 0.0011008 | 45421.8481 | 0.023644 | 1.6979 | 33.1103 | 38.5911 | 1.495 | 0.13483
2025-02-07 16:24 | 0.44747 | 0.50818 | 26.4584 | 0.023459 | 0.97863 | 0.49161 | 0.0010641 | 43906.4738 | 0.023644 | 1.6979 | 32.1581 | 37.4811 | 1.446 | 0.13041
2025-02-07 16:25 | 0.4467 | 0.5073 | 26.4582 | 0.023436 | 0.97863 | 0.49076 | 0.0010622 | 43830.6571 | 0.023645 | 1.6979 | 32.1104 | 37.4253 | 1.4423 | 0.13007
2025-02-07 16:26 | 0.44554 | 0.50598 | 26.4579 | 0.023537 | 0.97863 | 0.48948 | 0.0010595 | 43716.9229 | 0.023645 | 1.6979 | 32.0388 | 37.3415 | 1.4449 | 0.13031
2025-02-07 16:27 | 0.43627 | 0.49546 | 26.4574 | 0.023602 | 0.97863 | 0.4793 | 0.0010375 | 42807.626 | 0.023645 | 1.6978 | 31.4649 | 36.6722 | 1.4203 | 0.12809
2025-02-07 16:28 | 0.41928 | 0.47617 | 26.457 | 0.023416 | 0.97863 | 0.46064 | 0.00099706 | 41140.6774 | 0.023646 | 1.6978 | 30.4083 | 35.4404 | 1.357 | 0.12238
2025-02-07 16:29 | 0.41272 | 0.46871 | 26.4565 | 0.023338 | 0.97863 | 0.45343 | 0.00098145 | 40496.5682 | 0.023646 | 1.6978 | 29.9985 | 34.9624 | 1.3323 | 0.12016
2025-02-07 16:30 | 0.42623 | 0.48406 | 26.456 | 0.023383 | 0.97863 | 0.46828 | 0.0010136 | 41822.3569 | 0.023646 | 1.6978 | 30.8413 | 35.9442 | 1.3763 | 0.12412
2025-02-07 16:31 | 0.42816 | 0.48625 | 26.4556 | 0.02362 | 0.97863 | 0.4704 | 0.0010182 | 42011.6655 | 0.023646 | 1.6977 | 30.9613 | 36.0838 | 1.3962 | 0.12592
2025-02-07 16:32 | 0.43087 | 0.48931 | 26.4551 | 0.023505 | 0.97863 | 0.47337 | 0.0010246 | 42276.7382 | 0.023647 | 1.6977 | 31.1293 | 36.2792 | 1.3977 | 0.12606
2025-02-07 16:33 | 0.43859 | 0.49808 | 26.4549 | 0.023361 | 0.97863 | 0.48185 | 0.001043 | 43034.3402 | 0.023647 | 1.6977 | 31.6085 | 36.8374 | 1.4127 | 0.12741
2025-02-07 16:34 | 0.44168 | 0.50159 | 26.4549 | 0.023303 | 0.97863 | 0.48524 | 0.0010503 | 43337.3987 | 0.023647 | 1.6977 | 31.7999 | 37.0604 | 1.4187 | 0.12795
2025-02-07 16:35 | 0.42894 | 0.48712 | 26.4549 | 0.023329 | 0.97863 | 0.47125 | 0.00102 | 42087.2817 | 0.023647 | 1.6977 | 31.0094 | 36.1392 | 1.3813 | 0.12458
2025-02-07 16:36 | 0.42816 | 0.48624 | 26.4549 | 0.023437 | 0.97863 | 0.4704 | 0.0010182 | 42011.5167 | 0.023647 | 1.6977 | 30.9613 | 36.0832 | 1.3854 | 0.12494
2025-02-07 16:37 | 0.42508 | 0.48274 | 26.4549 | 0.023375 | 0.97863 | 0.467 | 0.0010108 | 41708.4586 | 0.023647 | 1.6977 | 30.7692 | 35.8593 | 1.3722 | 0.12376
2025-02-07 16:38 | 0.42083 | 0.47791 | 26.4549 | 0.023327 | 0.97863 | 0.46234 | 0.0010007 | 41291.752 | 0.023647 | 1.6977 | 30.5046 | 35.5509 | 1.3564 | 0.12233
2025-02-07 16:39 | 0.42237 | 0.47967 | 26.4549 | 0.023135 | 0.97863 | 0.46403 | 0.0010044 | 41443.2812 | 0.023647 | 1.6977 | 30.6009 | 35.6631 | 1.3499 | 0.12175
2025-02-07 16:40 | 0.42083 | 0.47791 | 26.455 | 0.023226 | 0.97863 | 0.46234 | 0.0010007 | 41291.7801 | 0.023647 | 1.6977 | 30.5046 | 35.551 | 1.3505 | 0.1218
2025-02-07 16:41 | 0.43009 | 0.48844 | 26.4553 | 0.023294 | 0.97863 | 0.47252 | 0.0010228 | 42201.0052 | 0.023647 | 1.6977 | 31.0814 | 36.2234 | 1.3828 | 0.12471
2025-02-07 16:42 | 0.43164 | 0.49019 | 26.4555 | 0.023391 | 0.97863 | 0.47421 | 0.0010264 | 42352.584 | 0.023647 | 1.6977 | 31.1773 | 36.3354 | 1.3933 | 0.12566
2025-02-07 16:43 | 0.41465 | 0.4709 | 26.4557 | 0.023359 | 0.97863 | 0.45555 | 0.00098604 | 40685.8049 | 0.023646 | 1.6978 | 30.1191 | 35.1023 | 1.3394 | 0.1208
2025-02-07 16:44 | 0.39844 | 0.45249 | 26.4559 | 0.02327 | 0.97863 | 0.43774 | 0.00094748 | 39094.7869 | 0.023646 | 1.6978 | 29.1034 | 33.9187 | 1.2847 | 0.11586
2025-02-07 16:45 | 0.39264 | 0.44591 | 26.4556 | 0.023305 | 0.97863 | 0.43137 | 0.00093371 | 38526.4884 | 0.023646 | 1.6978 | 28.7392 | 33.494 | 1.2689 | 0.11444
2025-02-07 16:46 | 0.40191 | 0.45643 | 26.455 | 0.02319 | 0.97863 | 0.44155 | 0.00095574 | 39435.5287 | 0.023647 | 1.6977 | 29.3215 | 34.1722 | 1.2909 | 0.11642
2025-02-07 16:47 | 0.41851 | 0.47528 | 26.4543 | 0.022996 | 0.97863 | 0.45979 | 0.00099522 | 41064.3257 | 0.023647 | 1.6977 | 30.3602 | 35.3821 | 1.3301 | 0.11996
2025-02-07 16:48 | 0.4077 | 0.463 | 26.4537 | 0.022785 | 0.97864 | 0.44792 | 0.00096952 | 40003.4844 | 0.023648 | 1.6977 | 29.6845 | 34.5941 | 1.2856 | 0.11595
2025-02-07 16:49 | 0.40963 | 0.46519 | 26.453 | 0.022861 | 0.97864 | 0.45004 | 0.00097411 | 40192.7538 | 0.023648 | 1.6976 | 29.8053 | 34.7344 | 1.2957 | 0.11685
2025-02-07 16:50 | 0.41426 | 0.47046 | 26.4532 | 0.022958 | 0.97864 | 0.45513 | 0.00098512 | 40647.3638 | 0.023648 | 1.6976 | 30.095 | 35.0721 | 1.3151 | 0.11861
2025-02-07 16:51 | 0.42469 | 0.4823 | 26.4538 | 0.023228 | 0.97864 | 0.46658 | 0.0010099 | 41670.3231 | 0.023648 | 1.6977 | 30.7451 | 35.8303 | 1.3624 | 0.12287
2025-02-07 16:52 | 0.4355 | 0.49457 | 26.4545 | 0.02312 | 0.97863 | 0.47846 | 0.0010356 | 42731.1704 | 0.023647 | 1.6977 | 31.417 | 36.6138 | 1.3888 | 0.12525
2025-02-07 16:53 | 0.43357 | 0.49238 | 26.4551 | 0.022987 | 0.97863 | 0.47634 | 0.001031 | 42541.9088 | 0.023647 | 1.6977 | 31.2972 | 36.4748 | 1.375 | 0.12401
2025-02-07 16:54 | 0.41928 | 0.47616 | 26.4557 | 0.023084 | 0.97863 | 0.46064 | 0.00099706 | 41140.4051 | 0.023646 | 1.6978 | 30.4083 | 35.4394 | 1.3377 | 0.12064
2025-02-07 16:55 | 0.41272 | 0.46871 | 26.4563 | 0.022896 | 0.97863 | 0.45343 | 0.00098145 | 40496.5187 | 0.023646 | 1.6978 | 29.9985 | 34.9622 | 1.307 | 0.11788
2025-02-07 16:56 | 0.41079 | 0.46652 | 26.4567 | 0.022784 | 0.97863 | 0.45131 | 0.00097686 | 40307.2057 | 0.023646 | 1.6978 | 29.8778 | 34.8219 | 1.2949 | 0.11679
2025-02-07 16:57 | 0.42585 | 0.48362 | 26.4572 | 0.022908 | 0.97863 | 0.46785 | 0.0010127 | 41784.7362 | 0.023645 | 1.6978 | 30.8172 | 35.9172 | 1.3472 | 0.12151
2025-02-07 16:58 | 0.45596 | 0.51782 | 26.4577 | 0.022991 | 0.97863 | 0.50094 | 0.0010843 | 44739.7075 | 0.023645 | 1.6978 | 32.6824 | 38.0914 | 1.4427 | 0.13011
2025-02-07 16:59 | 0.41658 | 0.4731 | 26.4581 | 0.022999 | 0.97863 | 0.45767 | 0.00099063 | 40875.7524 | 0.023645 | 1.6979 | 30.2397 | 35.2448 | 1.3247 | 0.11947
2025-02-07 17:00 | 0.39342 | 0.44679 | 26.4586 | 0.022934 | 0.97863 | 0.43222 | 0.00093555 | 38602.8688 | 0.023644 | 1.6979 | 28.7878 | 33.553 | 1.2511 | 0.11283
2025-02-07 17:01 | 0.39535 | 0.44899 | 26.459 | 0.022945 | 0.97862 | 0.43434 | 0.00094014 | 38792.381 | 0.023644 | 1.6979 | 28.9092 | 33.6949 | 1.2575 | 0.11342
2025-02-07 17:02 | 0.40732 | 0.46258 | 26.4592 | 0.023004 | 0.97862 | 0.44749 | 0.0009686 | 39966.8004 | 0.023644 | 1.6979 | 29.6603 | 34.5705 | 1.297 | 0.11697
2025-02-07 17:03 | 0.38994 | 0.44285 | 26.4592 | 0.02324 | 0.97862 | 0.42841 | 0.00092728 | 38262.0557 | 0.023644 | 1.6979 | 28.569 | 33.2985 | 1.2572 | 0.11338
2025-02-07 17:04 | 0.3884 | 0.44109 | 26.4592 | 0.02312 | 0.97862 | 0.42671 | 0.00092361 | 38110.523 | 0.023644 | 1.6979 | 28.4717 | 33.1851 | 1.246 | 0.11237
2025-02-07 17:05 | 0.40732 | 0.46258 | 26.4592 | 0.023017 | 0.97862 | 0.44749 | 0.0009686 | 39966.8 | 0.023644 | 1.6979 | 29.6603 | 34.5705 | 1.2977 | 0.11704
2025-02-07 17:06 | 0.41658 | 0.4731 | 26.4592 | 0.023039 | 0.97862 | 0.45767 | 0.00099063 | 40875.9969 | 0.023644 | 1.6979 | 30.2397 | 35.2458 | 1.327 | 0.11968
2025-02-07 17:07 | 0.39728 | 0.45118 | 26.4592 | 0.023051 | 0.97862 | 0.43646 | 0.00094473 | 38981.8354 | 0.023644 | 1.6979 | 29.0306 | 33.8365 | 1.2692 | 0.11447
2025-02-07 17:08 | 0.37952 | 0.43101 | 26.4592 | 0.023036 | 0.97862 | 0.41695 | 0.00090249 | 37239.2085 | 0.023644 | 1.6979 | 27.911 | 32.5315 | 1.2145 | 0.10953
2025-02-07 17:09 | 0.366 | 0.41566 | 26.4597 | 0.022801 | 0.97862 | 0.40211 | 0.00087036 | 35913.399 | 0.023644 | 1.6979 | 27.0542 | 31.5333 | 1.1614 | 0.10474
2025-02-07 17:10 | 0.36021 | 0.40909 | 26.4606 | 0.022757 | 0.97862 | 0.39574 | 0.00085659 | 35345.3132 | 0.023643 | 1.698 | 26.6856 | 31.1043 | 1.1418 | 0.10297
2025-02-07 17:11 | 0.35983 | 0.40865 | 26.4615 | 0.022835 | 0.97862 | 0.39532 | 0.00085567 | 35307.5937 | 0.023642 | 1.698 | 26.661 | 31.0763 | 1.1445 | 0.10322
2025-02-07 17:12 | 0.36871 | 0.41874 | 26.4623 | 0.022822 | 0.97862 | 0.40508 | 0.00087679 | 36179.0872 | 0.023642 | 1.6981 | 27.2259 | 31.7353 | 1.1707 | 0.10558
2025-02-07 17:13 | 0.38338 | 0.4354 | 26.4632 | 0.02278 | 0.97862 | 0.42119 | 0.00091168 | 37618.849 | 0.023641 | 1.6981 | 28.155 | 32.819 | 1.2128 | 0.10938
2025-02-07 17:14 | 0.39419 | 0.44768 | 26.4638 | 0.022841 | 0.97861 | 0.43307 | 0.00093738 | 38679.7276 | 0.023641 | 1.6981 | 28.8364 | 33.6138 | 1.2485 | 0.1126
2025-02-07 17:15 | 0.36755 | 0.41743 | 26.4642 | 0.02293 | 0.97861 | 0.4038 | 0.00087403 | 36065.804 | 0.02364 | 1.6981 | 27.1523 | 31.651 | 1.1728 | 0.10577
2025-02-07 17:16 | 0.35095 | 0.39857 | 26.4646 | 0.022915 | 0.97861 | 0.38556 | 0.00083456 | 34436.8605 | 0.02364 | 1.6982 | 26.0942 | 30.4179 | 1.1217 | 0.10116
2025-02-07 17:17 | 0.34863 | 0.39594 | 26.4651 | 0.022848 | 0.97861 | 0.38302 | 0.00082905 | 34209.6343 | 0.02364 | 1.6982 | 25.946 | 30.2454 | 1.1114 | 0.10024
2025-02-07 17:18 | 0.35674 | 0.40515 | 26.4655 | 0.023014 | 0.97861 | 0.39193 | 0.00084833 | 35005.2873 | 0.02364 | 1.6982 | 26.4641 | 30.8497 | 1.1442 | 0.10319
2025-02-07 17:19 | 0.35867 | 0.40735 | 26.4655 | 0.022857 | 0.97861 | 0.39405 | 0.00085292 | 35194.7173 | 0.023639 | 1.6982 | 26.5872 | 30.9932 | 1.1423 | 0.10302
2025-02-07 17:20 | 0.35944 | 0.40822 | 26.4653 | 0.022943 | 0.97861 | 0.3949 | 0.00085475 | 35270.4455 | 0.02364 | 1.6982 | 26.6364 | 31.0504 | 1.1489 | 0.10362
2025-02-07 17:21 | 0.35288 | 0.40077 | 26.4651 | 0.022967 | 0.97861 | 0.38769 | 0.00083915 | 34626.3684 | 0.02364 | 1.6982 | 26.2176 | 30.5621 | 1.1301 | 0.10192
2025-02-07 17:22 | 0.35133 | 0.39901 | 26.4649 | 0.022947 | 0.97861 | 0.38599 | 0.00083547 | 34474.7906 | 0.02364 | 1.6982 | 26.1189 | 30.4468 | 1.1244 | 0.10141
2025-02-07 17:23 | 0.35095 | 0.39857 | 26.4647 | 0.022819 | 0.97861 | 0.38556 | 0.00083456 | 34436.8661 | 0.02364 | 1.6982 | 26.0942 | 30.4179 | 1.117 | 0.10074
2025-02-07 17:24 | 0.34863 | 0.39594 | 26.4644 | 0.022911 | 0.97861 | 0.38302 | 0.00082905 | 34209.5204 | 0.02364 | 1.6981 | 25.946 | 30.245 | 1.1144 | 0.10051
2025-02-07 17:25 | 0.35481 | 0.40296 | 26.4642 | 0.022951 | 0.97861 | 0.38981 | 0.00084374 | 34815.628 | 0.02364 | 1.6981 | 26.3409 | 30.7052 | 1.1352 | 0.10238
2025-02-07 17:26 | 0.34631 | 0.39331 | 26.464 | 0.022877 | 0.97861 | 0.38047 | 0.00082354 | 33982.1357 | 0.023641 | 1.6981 | 25.7977 | 30.0718 | 1.1058 | 0.099727
2025-02-07 17:27 | 0.344 | 0.39068 | 26.4638 | 0.022787 | 0.97861 | 0.37793 | 0.00081803 | 33754.7913 | 0.023641 | 1.6981 | 25.6492 | 29.8986 | 1.0944 | 0.0987
2025-02-07 17:28 | 0.35404 | 0.40208 | 26.4636 | 0.022781 | 0.97862 | 0.38896 | 0.0008419 | 34739.7392 | 0.023641 | 1.6981 | 26.2916 | 30.6472 | 1.1244 | 0.10141
2025-02-07 17:29 | 0.35288 | 0.40077 | 26.4638 | 0.023006 | 0.97861 | 0.38769 | 0.00083915 | 34626.1222 | 0.023641 | 1.6981 | 26.2176 | 30.5611 | 1.132 | 0.10209
2025-02-07 17:30 | 0.3494 | 0.39682 | 26.4642 | 0.022877 | 0.97861 | 0.38387 | 0.00083088 | 34285.2449 | 0.02364 | 1.6981 | 25.9954 | 30.3024 | 1.1151 | 0.10057
2025-02-07 17:31 | 0.35404 | 0.40208 | 26.4646 | 0.022759 | 0.97861 | 0.38896 | 0.0008419 | 34739.9363 | 0.02364 | 1.6982 | 26.2916 | 30.648 | 1.1234 | 0.10131
2025-02-07 17:32 | 0.35481 | 0.40296 | 26.4651 | 0.022513 | 0.97861 | 0.38981 | 0.00084374 | 34815.7859 | 0.02364 | 1.6982 | 26.3409 | 30.7058 | 1.1136 | 0.10043
2025-02-07 17:33 | 0.35404 | 0.40208 | 26.4655 | 0.022502 | 0.97861 | 0.38896 | 0.0008419 | 34740.0983 | 0.023639 | 1.6982 | 26.2916 | 30.6486 | 1.1107 | 0.10017
2025-02-07 17:34 | 0.37604 | 0.42708 | 26.4661 | 0.022494 | 0.97861 | 0.41314 | 0.00089423 | 36899.6281 | 0.023639 | 1.6982 | 27.6911 | 32.2804 | 1.1758 | 0.10605
2025-02-07 17:35 | 0.39728 | 0.4512 | 26.4667 | 0.022561 | 0.97861 | 0.43646 | 0.00094473 | 38983.4184 | 0.023639 | 1.6982 | 29.0306 | 33.8425 | 1.2425 | 0.11206
2025-02-07 17:36 | 0.3911 | 0.44418 | 26.4673 | 0.022715 | 0.97861 | 0.42968 | 0.00093004 | 38377.3965 | 0.023638 | 1.6983 | 28.642 | 33.39 | 1.2326 | 0.11116
2025-02-07 17:37 | 0.39959 | 0.45383 | 26.468 | 0.022691 | 0.97861 | 0.43901 | 0.00095024 | 39211.0024 | 0.023638 | 1.6983 | 29.1761 | 34.0132 | 1.2567 | 0.11334
2025-02-07 17:38 | 0.41349 | 0.46962 | 26.4686 | 0.022669 | 0.9786 | 0.45428 | 0.00098329 | 40575.0055 | 0.023637 | 1.6983 | 30.0468 | 35.0287 | 1.2969 | 0.11696
2025-02-07 17:39 | 0.42353 | 0.48102 | 26.4691 | 0.022674 | 0.9786 | 0.46531 | 0.0010072 | 41560.1342 | 0.023637 | 1.6984 | 30.673 | 35.7592 | 1.327 | 0.11968
2025-02-07 17:40 | 0.42237 | 0.47971 | 26.4696 | 0.022742 | 0.9786 | 0.46403 | 0.0010044 | 41446.574 | 0.023637 | 1.6984 | 30.6009 | 35.6755 | 1.3276 | 0.11973
2025-02-07 17:41 | 0.41118 | 0.46699 | 26.47 | 0.022765 | 0.9786 | 0.45173 | 0.00097778 | 40347.9932 | 0.023636 | 1.6984 | 29.9019 | 34.861 | 1.2955 | 0.11683
2025-02-07 17:42 | 0.405 | 0.45998 | 26.4704 | 0.022765 | 0.9786 | 0.44495 | 0.00096309 | 39741.9191 | 0.023636 | 1.6984 | 29.5152 | 34.4105 | 1.277 | 0.11517
2025-02-07 17:43 | 0.39226 | 0.44551 | 26.4709 | 0.022765 | 0.9786 | 0.43095 | 0.00093279 | 38491.7859 | 0.023636 | 1.6984 | 28.7149 | 33.4778 | 1.2388 | 0.11173
2025-02-07 17:44 | 0.37064 | 0.42095 | 26.4709 | 0.022757 | 0.9786 | 0.4072 | 0.00088138 | 36370.2023 | 0.023636 | 1.6984 | 27.3484 | 31.8847 | 1.1735 | 0.10583
2025-02-07 17:45 | 0.37257 | 0.42314 | 26.4708 | 0.022645 | 0.9786 | 0.40932 | 0.00088597 | 36559.6007 | 0.023636 | 1.6984 | 27.4709 | 32.0273 | 1.1735 | 0.10584
2025-02-07 17:46 | 0.37527 | 0.42621 | 26.4706 | 0.022526 | 0.9786 | 0.41229 | 0.0008924 | 36824.7702 | 0.023636 | 1.6984 | 27.6421 | 32.2269 | 1.1754 | 0.106
2025-02-07 17:47 | 0.37141 | 0.42183 | 26.4705 | 0.022701 | 0.9786 | 0.40805 | 0.00088321 | 36445.8837 | 0.023636 | 1.6984 | 27.3974 | 31.9415 | 1.1729 | 0.10578
2025-02-07 17:48 | 0.36407 | 0.4135 | 26.4703 | 0.022762 | 0.9786 | 0.39999 | 0.00086577 | 35726.0283 | 0.023636 | 1.6984 | 26.9314 | 31.398 | 1.154 | 0.10407
2025-02-07 17:49 | 0.35944 | 0.40823 | 26.4701 | 0.022725 | 0.9786 | 0.3949 | 0.00085475 | 35271.3725 | 0.023636 | 1.6984 | 26.6364 | 31.054 | 1.1381 | 0.10265
2025-02-07 17:50 | 0.36253 | 0.41174 | 26.47 | 0.022677 | 0.9786 | 0.39829 | 0.0008621 | 35574.4268 | 0.023636 | 1.6984 | 26.8331 | 31.2833 | 1.145 | 0.10327
2025-02-07 17:51 | 0.36485 | 0.41437 | 26.4701 | 0.022629 | 0.9786 | 0.40083 | 0.00086761 | 35801.7554 | 0.023636 | 1.6984 | 26.9805 | 31.4551 | 1.1496 | 0.10368
2025-02-07 17:52 | 0.36253 | 0.41174 | 26.4703 | 0.022576 | 0.9786 | 0.39829 | 0.0008621 | 35574.484 | 0.023636 | 1.6984 | 26.8331 | 31.2835 | 1.1399 | 0.10281
2025-02-07 17:53 | 0.38415 | 0.4363 | 26.4705 | 0.022465 | 0.9786 | 0.42204 | 0.00091351 | 37696.1161 | 0.023636 | 1.6984 | 28.2037 | 32.8816 | 1.1985 | 0.10809
2025-02-07 17:54 | 0.39149 | 0.44463 | 26.4707 | 0.022481 | 0.9786 | 0.4301 | 0.00093096 | 38415.9867 | 0.023636 | 1.6984 | 28.6663 | 33.421 | 1.2211 | 0.11013
2025-02-07 17:55 | 0.36755 | 0.41744 | 26.4709 | 0.022643 | 0.9786 | 0.4038 | 0.00087403 | 36067.1213 | 0.023636 | 1.6984 | 27.1523 | 31.6561 | 1.1583 | 0.10447
2025-02-07 17:56 | 0.35481 | 0.40297 | 26.4707 | 0.022431 | 0.9786 | 0.38981 | 0.00084374 | 34816.8568 | 0.023636 | 1.6984 | 26.3409 | 30.7099 | 1.1097 | 0.10008
2025-02-07 17:57 | 0.36176 | 0.41086 | 26.4703 | 0.022471 | 0.9786 | 0.39744 | 0.00086026 | 35498.7157 | 0.023636 | 1.6984 | 26.784 | 31.2262 | 1.1323 | 0.10212
2025-02-07 17:58 | 0.38106 | 0.43279 | 26.4699 | 0.022346 | 0.9786 | 0.41865 | 0.00090617 | 37392.9033 | 0.023636 | 1.6984 | 28.0086 | 32.6536 | 1.183 | 0.10669
2025-02-07 17:59 | 0.38724 | 0.4398 | 26.4694 | 0.022363 | 0.9786 | 0.42544 | 0.00092086 | 37998.9802 | 0.023637 | 1.6984 | 28.3986 | 33.108 | 1.2021 | 0.10842
2025-02-07 18:00 | 0.38068 | 0.43235 | 26.469 | 0.022389 | 0.9786 | 0.41823 | 0.00090525 | 37354.8486 | 0.023637 | 1.6984 | 27.9842 | 32.6245 | 1.1841 | 0.10679
2025-02-07 18:01 | 0.36755 | 0.41744 | 26.4696 | 0.02245 | 0.9786 | 0.4038 | 0.00087403 | 36066.8576 | 0.023637 | 1.6984 | 27.1523 | 31.655 | 1.1484 | 0.10357
2025-02-07 18:02 | 0.35095 | 0.39859 | 26.4707 | 0.022377 | 0.9786 | 0.38556 | 0.00083456 | 34437.9867 | 0.023636 | 1.6984 | 26.0942 | 30.4222 | 1.0956 | 0.098806
2025-02-07 18:03 | 0.34863 | 0.39596 | 26.4717 | 0.022483 | 0.9786 | 0.38302 | 0.00082905 | 34210.8725 | 0.023635 | 1.6985 | 25.946 | 30.2502 | 1.0939 | 0.098653
2025-02-07 18:04 | 0.34902 | 0.3964 | 26.4728 | 0.022489 | 0.9786 | 0.38344 | 0.00082996 | 34248.9575 | 0.023634 | 1.6985 | 25.9707 | 30.2798 | 1.0953 | 0.098784
2025-02-07 18:05 | 0.32662 | 0.37097 | 26.4739 | 0.022476 | 0.97859 | 0.35884 | 0.00077671 | 32051.7538 | 0.023634 | 1.6986 | 24.5311 | 28.6021 | 1.0278 | 0.092697
2025-02-07 18:06 | 0.32392 | 0.3679 | 26.4745 | 0.022429 | 0.97859 | 0.35587 | 0.00077029 | 31786.6622 | 0.023633 | 1.6986 | 24.3565 | 28.3989 | 1.0177 | 0.09178
2025-02-07 18:07 | 0.34091 | 0.3872 | 26.4749 | 0.022289 | 0.97859 | 0.37454 | 0.00081068 | 33453.7412 | 0.023633 | 1.6986 | 25.451 | 29.6754 | 1.0617 | 0.095751
2025-02-07 18:08 | 0.34593 | 0.3929 | 26.4754 | 0.022344 | 0.97859 | 0.38005 | 0.00082262 | 33946.3437 | 0.023633 | 1.6986 | 25.7729 | 30.0511 | 1.0792 | 0.097332
2025-02-07 18:09 | 0.34709 | 0.39421 | 26.4758 | 0.02227 | 0.97859 | 0.38132 | 0.00082537 | 34060.0816 | 0.023632 | 1.6987 | 25.8471 | 30.1379 | 1.0791 | 0.09732
2025-02-07 18:10 | 0.3355 | 0.38106 | 26.4762 | 0.022249 | 0.97859 | 0.3686 | 0.00079783 | 32923.5579 | 0.023632 | 1.6987 | 25.1036 | 29.2712 | 1.0438 | 0.09414
2025-02-07 18:11 | 0.34207 | 0.38851 | 26.4761 | 0.022347 | 0.97859 | 0.37581 | 0.00081344 | 33567.6087 | 0.023632 | 1.6987 | 25.5254 | 29.7629 | 1.0679 | 0.096313
2025-02-07 18:12 | 0.34554 | 0.39246 | 26.4757 | 0.022322 | 0.97859 | 0.37963 | 0.0008217 | 33908.5094 | 0.023632 | 1.6987 | 25.7482 | 30.0224 | 1.077 | 0.097135
2025-02-07 18:13 | 0.3467 | 0.39377 | 26.4752 | 0.022473 | 0.97859 | 0.3809 | 0.00082446 | 34022.0896 | 0.023633 | 1.6986 | 25.8224 | 30.1086 | 1.0877 | 0.098099
2025-02-07 18:14 | 0.35983 | 0.40868 | 26.4748 | 0.022501 | 0.97859 | 0.39532 | 0.00085567 | 35310.1483 | 0.023633 | 1.6986 | 26.661 | 31.0861 | 1.1282 | 0.10175
2025-02-07 18:15 | 0.35712 | 0.40561 | 26.4744 | 0.022615 | 0.97859 | 0.39235 | 0.00084924 | 35044.864 | 0.023633 | 1.6986 | 26.4887 | 30.8849 | 1.1258 | 0.10154
2025-02-07 18:16 | 0.344 | 0.3907 | 26.4743 | 0.022475 | 0.97859 | 0.37793 | 0.00081803 | 33756.7208 | 0.023633 | 1.6986 | 25.6492 | 29.906 | 1.0798 | 0.09738
2025-02-07 18:17 | 0.35018 | 0.39772 | 26.4745 | 0.022409 | 0.97859 | 0.38472 | 0.00083272 | 34362.9301 | 0.023633 | 1.6986 | 26.0448 | 30.3674 | 1.0949 | 0.098748
2025-02-07 18:18 | 0.34361 | 0.39026 | 26.4746 | 0.022567 | 0.97859 | 0.37751 | 0.00081711 | 33718.8906 | 0.023633 | 1.6986 | 25.6244 | 29.8774 | 1.083 | 0.097676
2025-02-07 18:19 | 0.33628 | 0.38193 | 26.4748 | 0.022539 | 0.97859 | 0.36945 | 0.00079967 | 32999.0764 | 0.023633 | 1.6986 | 25.1533 | 29.3281 | 1.0597 | 0.095572
2025-02-07 18:20 | 0.34902 | 0.3964 | 26.475 | 0.02245 | 0.97859 | 0.38344 | 0.00082996 | 34249.3563 | 0.023633 | 1.6986 | 25.9707 | 30.2814 | 1.0935 | 0.098621
2025-02-07 18:21 | 0.36485 | 0.41438 | 26.4751 | 0.022415 | 0.97859 | 0.40083 | 0.00086761 | 35802.7309 | 0.023633 | 1.6986 | 26.9805 | 31.4589 | 1.1388 | 0.10271
2025-02-07 18:22 | 0.34709 | 0.39421 | 26.4752 | 0.02224 | 0.97859 | 0.38132 | 0.00082537 | 34059.9779 | 0.023633 | 1.6986 | 25.8471 | 30.1375 | 1.0776 | 0.097186
2025-02-07 18:23 | 0.32392 | 0.3679 | 26.4749 | 0.022196 | 0.97859 | 0.35587 | 0.00077029 | 31786.7217 | 0.023633 | 1.6986 | 24.3565 | 28.3991 | 1.0071 | 0.090825
2025-02-07 18:24 | 0.31041 | 0.35255 | 26.4742 | 0.022227 | 0.97859 | 0.34103 | 0.00073815 | 30460.5899 | 0.023633 | 1.6986 | 23.48 | 27.3768 | 0.96842 | 0.08734
2025-02-07 18:25 | 0.32971 | 0.37448 | 26.4736 | 0.022205 | 0.97859 | 0.36224 | 0.00078406 | 32354.7922 | 0.023634 | 1.6986 | 24.7305 | 28.8343 | 1.0246 | 0.092405
2025-02-07 18:26 | 0.36446 | 0.41394 | 26.4729 | 0.022227 | 0.9786 | 0.40041 | 0.00086669 | 35764.4241 | 0.023634 | 1.6985 | 26.956 | 31.4286 | 1.1281 | 0.10174
2025-02-07 18:27 | 0.36948 | 0.41964 | 26.4723 | 0.022199 | 0.9786 | 0.40592 | 0.00087862 | 36256.8207 | 0.023635 | 1.6985 | 27.2749 | 31.8 | 1.1413 | 0.10294
2025-02-07 18:28 | 0.35944 | 0.40824 | 26.4724 | 0.022167 | 0.9786 | 0.3949 | 0.00085475 | 35271.7994 | 0.023635 | 1.6985 | 26.6364 | 31.0557 | 1.1103 | 0.10013
2025-02-07 18:29 | 0.36253 | 0.41175 | 26.4728 | 0.022288 | 0.9786 | 0.39829 | 0.0008621 | 35574.969 | 0.023634 | 1.6985 | 26.8331 | 31.2853 | 1.1254 | 0.1015
2025-02-07 18:30 | 0.35712 | 0.40561 | 26.4732 | 0.022231 | 0.9786 | 0.39235 | 0.00084924 | 35044.6472 | 0.023634 | 1.6985 | 26.4887 | 30.8841 | 1.1067 | 0.099807
2025-02-07 18:31 | 0.33242 | 0.37755 | 26.4737 | 0.0223 | 0.97859 | 0.3652 | 0.00079049 | 32620.0126 | 0.023634 | 1.6986 | 24.9047 | 29.0375 | 1.037 | 0.093525
2025-02-07 18:32 | 0.33396 | 0.3793 | 26.4741 | 0.022275 | 0.97859 | 0.3669 | 0.00079416 | 32771.6325 | 0.023633 | 1.6986 | 25.0042 | 29.1538 | 1.0404 | 0.093833
2025-02-07 18:33 | 0.3494 | 0.39684 | 26.4744 | 0.022412 | 0.97859 | 0.38387 | 0.00083088 | 34287.1368 | 0.023633 | 1.6986 | 25.9954 | 30.3098 | 1.0928 | 0.098556
2025-02-07 18:34 | 0.36176 | 0.41087 | 26.4746 | 0.022246 | 0.97859 | 0.39744 | 0.00086026 | 35499.5418 | 0.023633 | 1.6986 | 26.784 | 31.2293 | 1.1211 | 0.10111
2025-02-07 18:35 | 0.35983 | 0.40868 | 26.4748 | 0.022206 | 0.97859 | 0.39532 | 0.00085567 | 35310.1521 | 0.023633 | 1.6986 | 26.661 | 31.0861 | 1.1134 | 0.10042
2025-02-07 18:36 | 0.33242 | 0.37755 | 26.475 | 0.022326 | 0.97859 | 0.3652 | 0.00079049 | 32620.253 | 0.023633 | 1.6986 | 24.9047 | 29.0385 | 1.0383 | 0.093638
2025-02-07 18:37 | 0.34361 | 0.39027 | 26.4752 | 0.022196 | 0.97859 | 0.37751 | 0.00081711 | 33718.9944 | 0.023633 | 1.6986 | 25.6244 | 29.8778 | 1.0652 | 0.096069
2025-02-07 18:38 | 0.36871 | 0.41877 | 26.4744 | 0.022555 | 0.97859 | 0.40508 | 0.00087679 | 36181.4676 | 0.023633 | 1.6986 | 27.2259 | 31.7445 | 1.1574 | 0.10439
2025-02-07 18:39 | 0.36214 | 0.41131 | 26.4732 | 0.022214 | 0.9786 | 0.39787 | 0.00086118 | 35537.1629 | 0.023634 | 1.6985 | 26.8085 | 31.257 | 1.1206 | 0.10106
2025-02-07 18:40 | 0.35481 | 0.40298 | 26.472 | 0.022104 | 0.9786 | 0.38981 | 0.00084374 | 34817.0949 | 0.023635 | 1.6985 | 26.3409 | 30.7108 | 1.0935 | 0.098623
2025-02-07 18:41 | 0.33859 | 0.38456 | 26.4708 | 0.022167 | 0.9786 | 0.37199 | 0.00080518 | 33225.6689 | 0.023636 | 1.6984 | 25.3022 | 29.499 | 1.0489 | 0.094601
2025-02-07 18:42 | 0.30423 | 0.34553 | 26.4695 | 0.022115 | 0.9786 | 0.33424 | 0.00072346 | 29853.6523 | 0.023637 | 1.6984 | 23.0776 | 26.9046 | 0.94514 | 0.08524
2025-02-07 18:43 | 0.29998 | 0.3407 | 26.4683 | 0.022104 | 0.97861 | 0.32957 | 0.00071337 | 29436.7175 | 0.023638 | 1.6983 | 22.8003 | 26.5806 | 0.93208 | 0.084062
2025-02-07 18:44 | 0.33782 | 0.38367 | 26.4671 | 0.022178 | 0.97861 | 0.37114 | 0.00080334 | 33149.2441 | 0.023638 | 1.6983 | 25.2526 | 29.4386 | 1.047 | 0.09443
2025-02-07 18:45 | 0.34902 | 0.39639 | 26.4675 | 0.022248 | 0.97861 | 0.38344 | 0.00082996 | 34247.9679 | 0.023638 | 1.6983 | 25.9707 | 30.276 | 1.0835 | 0.097714
2025-02-07 18:46 | 0.34014 | 0.38631 | 26.4685 | 0.022413 | 0.9786 | 0.37369 | 0.00080885 | 33376.8097 | 0.023637 | 1.6983 | 25.4014 | 29.6131 | 1.0651 | 0.096057
2025-02-07 18:47 | 0.33319 | 0.37842 | 26.4696 | 0.022243 | 0.9786 | 0.36605 | 0.00079232 | 32695.0671 | 0.023637 | 1.6984 | 24.9545 | 29.0928 | 1.0365 | 0.093479
2025-02-07 18:48 | 0.31581 | 0.35869 | 26.4707 | 0.022157 | 0.9786 | 0.34697 | 0.00075101 | 30990.4056 | 0.023636 | 1.6984 | 23.8312 | 27.784 | 0.98125 | 0.088496
2025-02-07 18:49 | 0.31427 | 0.35693 | 26.4717 | 0.02218 | 0.9786 | 0.34527 | 0.00074734 | 30839.038 | 0.023635 | 1.6985 | 23.731 | 27.6678 | 0.97772 | 0.088178
2025-02-07 18:50 | 0.31581 | 0.35869 | 26.4719 | 0.022157 | 0.9786 | 0.34697 | 0.00075101 | 30990.6038 | 0.023635 | 1.6985 | 23.8312 | 27.7848 | 0.98128 | 0.0885
2025-02-07 18:51 | 0.3162 | 0.35913 | 26.4716 | 0.022183 | 0.9786 | 0.34739 | 0.00075193 | 31028.4376 | 0.023635 | 1.6985 | 23.8563 | 27.8138 | 0.98358 | 0.088707
2025-02-07 18:52 | 0.32238 | 0.36614 | 26.4713 | 0.022207 | 0.9786 | 0.35418 | 0.00076662 | 31634.5577 | 0.023635 | 1.6985 | 24.2566 | 28.2802 | 1.0029 | 0.090451
2025-02-07 18:53 | 0.30616 | 0.34772 | 26.471 | 0.022334 | 0.9786 | 0.33636 | 0.00072806 | 30043.308 | 0.023636 | 1.6984 | 23.2035 | 27.0523 | 0.96032 | 0.086609
2025-02-07 18:54 | 0.28724 | 0.32624 | 26.4706 | 0.0222 | 0.9786 | 0.31558 | 0.00068307 | 28186.8642 | 0.023636 | 1.6984 | 21.965 | 25.6082 | 0.89832 | 0.081017
2025-02-07 18:55 | 0.29304 | 0.33281 | 26.4703 | 0.021929 | 0.9786 | 0.32194 | 0.00069684 | 28755.1002 | 0.023636 | 1.6984 | 22.3453 | 26.0514 | 0.90436 | 0.081562
2025-02-07 18:56 | 0.29342 | 0.33325 | 26.47 | 0.021984 | 0.9786 | 0.32236 | 0.00069776 | 28792.9392 | 0.023636 | 1.6984 | 22.3706 | 26.0807 | 0.90774 | 0.081866
2025-02-07 18:57 | 0.27682 | 0.3144 | 26.4699 | 0.022065 | 0.9786 | 0.30413 | 0.00065828 | 27163.8514 | 0.023636 | 1.6984 | 21.2777 | 24.8065 | 0.86195 | 0.077737
2025-02-07 18:58 | 0.27643 | 0.31396 | 26.4699 | 0.021959 | 0.9786 | 0.3037 | 0.00065736 | 27125.966 | 0.023636 | 1.6984 | 21.2522 | 24.7767 | 0.85665 | 0.077259
2025-02-07 18:59 | 0.28145 | 0.31966 | 26.4699 | 0.022099 | 0.9786 | 0.30922 | 0.0006693 | 27618.4761 | 0.023636 | 1.6984 | 21.5836 | 25.1631 | 0.87701 | 0.079095
2025-02-07 19:00 | 0.28107 | 0.31922 | 26.4699 | 0.022105 | 0.9786 | 0.30879 | 0.00066838 | 27580.5916 | 0.023636 | 1.6984 | 21.5582 | 25.1334 | 0.87613 | 0.079016
2025-02-07 19:01 | 0.28802 | 0.32711 | 26.4699 | 0.022093 | 0.9786 | 0.31643 | 0.0006849 | 28262.529 | 0.023636 | 1.6984 | 22.0158 | 25.6669 | 0.89626 | 0.080831
2025-02-07 19:02 | 0.27682 | 0.3144 | 26.4699 | 0.022054 | 0.9786 | 0.30413 | 0.00065828 | 27163.8514 | 0.023636 | 1.6984 | 21.2777 | 24.8065 | 0.86151 | 0.077698
2025-02-07 19:03 | 0.29381 | 0.33369 | 26.4699 | 0.02201 | 0.9786 | 0.32279 | 0.00069868 | 28830.8082 | 0.023636 | 1.6984 | 22.396 | 26.1102 | 0.90997 | 0.082068
2025-02-07 19:04 | 0.33473 | 0.38017 | 26.4695 | 0.022016 | 0.9786 | 0.36775 | 0.00079599 | 32846.5832 | 0.023637 | 1.6984 | 25.0539 | 29.2086 | 1.0305 | 0.092934
2025-02-07 19:05 | 0.33898 | 0.38499 | 26.4688 | 0.022158 | 0.9786 | 0.37242 | 0.00080609 | 33263.2057 | 0.023637 | 1.6983 | 25.327 | 29.5266 | 1.0496 | 0.09466
2025-02-07 19:06 | 0.31427 | 0.35693 | 26.4682 | 0.022181 | 0.97861 | 0.34527 | 0.00074734 | 30838.4445 | 0.023638 | 1.6983 | 23.731 | 27.6655 | 0.97767 | 0.088174
2025-02-07 19:07 | 0.29304 | 0.33281 | 26.4676 | 0.022075 | 0.97861 | 0.32194 | 0.00069684 | 28754.6658 | 0.023638 | 1.6983 | 22.3453 | 26.0497 | 0.91029 | 0.082097
2025-02-07 19:08 | 0.29535 | 0.33544 | 26.4669 | 0.022046 | 0.97861 | 0.32448 | 0.00070235 | 28981.8759 | 0.023638 | 1.6983 | 22.4972 | 26.2263 | 0.91591 | 0.082604
2025-02-07 19:09 | 0.28338 | 0.32184 | 26.4666 | 0.022006 | 0.97861 | 0.31134 | 0.00067389 | 27807.3945 | 0.023639 | 1.6982 | 21.7109 | 25.3095 | 0.87894 | 0.079269
2025-02-07 19:10 | 0.29535 | 0.33544 | 26.4664 | 0.021966 | 0.97861 | 0.32448 | 0.00070235 | 28981.7881 | 0.023639 | 1.6982 | 22.4972 | 26.2259 | 0.91258 | 0.082304
2025-02-07 19:11 | 0.31388 | 0.35648 | 26.4661 | 0.022006 | 0.97861 | 0.34484 | 0.00074642 | 30800.2171 | 0.023639 | 1.6982 | 23.7059 | 27.6349 | 0.96874 | 0.087368
2025-02-07 19:12 | 0.30771 | 0.34947 | 26.4659 | 0.022117 | 0.97861 | 0.33806 | 0.00073173 | 30194.0268 | 0.023639 | 1.6982 | 23.3041 | 27.1664 | 0.95539 | 0.086165
2025-02-07 19:13 | 0.29304 | 0.33281 | 26.4657 | 0.022093 | 0.97861 | 0.32194 | 0.00069684 | 28754.378 | 0.023639 | 1.6982 | 22.3453 | 26.0485 | 0.911 | 0.082161
2025-02-07 19:14 | 0.27257 | 0.30957 | 26.4653 | 0.02197 | 0.97861 | 0.29946 | 0.00064818 | 26746.444 | 0.02364 | 1.6982 | 20.9967 | 24.4762 | 0.84556 | 0.076259
2025-02-07 19:15 | 0.28184 | 0.32009 | 26.4649 | 0.021886 | 0.97861 | 0.30964 | 0.00067021 | 27655.6063 | 0.02364 | 1.6982 | 21.6091 | 25.1898 | 0.86959 | 0.078426
2025-02-07 19:16 | 0.30269 | 0.34376 | 26.4645 | 0.021986 | 0.97861 | 0.33254 | 0.00071979 | 29701.2942 | 0.02364 | 1.6981 | 22.9769 | 26.7839 | 0.93494 | 0.08432
2025-02-07 19:17 | 0.3108 | 0.35297 | 26.464 | 0.022065 | 0.97861 | 0.34145 | 0.00073907 | 30496.7945 | 0.023641 | 1.6981 | 23.5052 | 27.3995 | 0.96221 | 0.086779
2025-02-07 19:18 | 0.28802 | 0.3271 | 26.4636 | 0.021942 | 0.97861 | 0.31643 | 0.0006849 | 28261.5632 | 0.023641 | 1.6981 | 22.0158 | 25.6631 | 0.88996 | 0.080263
2025-02-07 19:19 | 0.27682 | 0.31439 | 26.4638 | 0.021922 | 0.97861 | 0.30413 | 0.00065828 | 27162.9495 | 0.023641 | 1.6981 | 21.2777 | 24.8029 | 0.85621 | 0.077219
2025-02-07 19:20 | 0.28802 | 0.3271 | 26.4642 | 0.021723 | 0.97861 | 0.31643 | 0.0006849 | 28261.657 | 0.02364 | 1.6981 | 22.0158 | 25.6635 | 0.88111 | 0.079465
2025-02-07 19:21 | 0.30346 | 0.34464 | 26.4647 | 0.021767 | 0.97861 | 0.33339 | 0.00072163 | 29777.0958 | 0.02364 | 1.6982 | 23.0273 | 26.8428 | 0.9279 | 0.083685
2025-02-07 19:22 | 0.28917 | 0.32842 | 26.4651 | 0.021962 | 0.97861 | 0.3177 | 0.00068766 | 28375.4408 | 0.02364 | 1.6982 | 22.0919 | 25.7527 | 0.89421 | 0.080647
2025-02-07 19:23 | 0.28223 | 0.32053 | 26.4655 | 0.021986 | 0.97861 | 0.31006 | 0.00067113 | 27693.5832 | 0.023639 | 1.6982 | 21.6345 | 25.2198 | 0.87469 | 0.078887
2025-02-07 19:24 | 0.27643 | 0.31395 | 26.4653 | 0.021839 | 0.97861 | 0.3037 | 0.00065736 | 27125.2883 | 0.02364 | 1.6982 | 21.2522 | 24.774 | 0.85185 | 0.076826
2025-02-07 19:25 | 0.28917 | 0.32842 | 26.4649 | 0.02178 | 0.97861 | 0.3177 | 0.00068766 | 28375.4096 | 0.02364 | 1.6982 | 22.0919 | 25.7526 | 0.88678 | 0.079977
2025-02-07 19:26 | 0.29767 | 0.33806 | 26.4645 | 0.021852 | 0.97861 | 0.32703 | 0.00070786 | 29208.7985 | 0.02364 | 1.6981 | 22.6488 | 26.4015 | 0.91459 | 0.082485
2025-02-07 19:27 | 0.29998 | 0.34069 | 26.464 | 0.021952 | 0.97861 | 0.32957 | 0.00071337 | 29436.0354 | 0.023641 | 1.6981 | 22.8003 | 26.5779 | 0.92556 | 0.083474
2025-02-07 19:28 | 0.29574 | 0.33587 | 26.4636 | 0.022057 | 0.97862 | 0.32491 | 0.00070327 | 29019.2407 | 0.023641 | 1.6981 | 22.5224 | 26.2537 | 0.91743 | 0.082741
2025-02-07 19:29 | 0.30307 | 0.3442 | 26.463 | 0.021932 | 0.97862 | 0.33297 | 0.00072071 | 29738.9442 | 0.023641 | 1.6981 | 23.0021 | 26.8124 | 0.93375 | 0.084213
2025-02-07 19:30 | 0.31157 | 0.35385 | 26.4624 | 0.021849 | 0.97862 | 0.3423 | 0.00074091 | 30572.2857 | 0.023642 | 1.6981 | 23.5554 | 27.4569 | 0.95497 | 0.086127
2025-02-07 19:31 | 0.31002 | 0.35209 | 26.4617 | 0.021716 | 0.97862 | 0.3406 | 0.00073724 | 30420.6446 | 0.023642 | 1.698 | 23.4549 | 27.3394 | 0.94466 | 0.085197
2025-02-07 19:32 | 0.29844 | 0.33894 | 26.4611 | 0.021837 | 0.97862 | 0.32788 | 0.00070969 | 29284.03 | 0.023643 | 1.698 | 22.6993 | 26.4583 | 0.91612 | 0.082623
2025-02-07 19:33 | 0.29728 | 0.33762 | 26.4604 | 0.021913 | 0.97862 | 0.32661 | 0.00070694 | 29170.2769 | 0.023643 | 1.698 | 22.6236 | 26.3696 | 0.91588 | 0.082601
2025-02-07 19:34 | 0.29381 | 0.33367 | 26.4597 | 0.021731 | 0.97862 | 0.32279 | 0.00069868 | 28829.2115 | 0.023644 | 1.6979 | 22.396 | 26.1038 | 0.89814 | 0.081001
2025-02-07 19:35 | 0.29458 | 0.33455 | 26.4589 | 0.021807 | 0.97862 | 0.32364 | 0.00070051 | 28904.8579 | 0.023644 | 1.6979 | 22.4466 | 26.1623 | 0.90352 | 0.081486
2025-02-07 19:36 | 0.29188 | 0.33148 | 26.4582 | 0.021671 | 0.97863 | 0.32067 | 0.00069409 | 28639.557 | 0.023645 | 1.6979 | 22.2693 | 25.9553 | 0.89004 | 0.08027
2025-02-07 19:37 | 0.28609 | 0.3249 | 26.4574 | 0.021749 | 0.97863 | 0.31431 | 0.00068031 | 28071.1948 | 0.023645 | 1.6978 | 21.8888 | 25.5114 | 0.87635 | 0.079036
2025-02-07 19:38 | 0.28377 | 0.32227 | 26.4566 | 0.021835 | 0.97863 | 0.31176 | 0.00067481 | 27843.7818 | 0.023646 | 1.6978 | 21.7363 | 25.3331 | 0.87299 | 0.078733
2025-02-07 19:39 | 0.29767 | 0.33805 | 26.4559 | 0.021774 | 0.97863 | 0.32703 | 0.00070786 | 29207.4374 | 0.023646 | 1.6978 | 22.6488 | 26.3962 | 0.91109 | 0.082169
2025-02-07 19:40 | 0.29805 | 0.33849 | 26.4551 | 0.021728 | 0.97863 | 0.32745 | 0.00070878 | 29245.2022 | 0.023647 | 1.6977 | 22.6741 | 26.4251 | 0.91025 | 0.082093
2025-02-07 19:41 | 0.30655 | 0.34813 | 26.4552 | 0.021751 | 0.97863 | 0.33679 | 0.00072897 | 30078.616 | 0.023647 | 1.6977 | 23.2287 | 27.0715 | 0.93594 | 0.08441
2025-02-07 19:42 | 0.31427 | 0.3569 | 26.4555 | 0.021732 | 0.97863 | 0.34527 | 0.00074734 | 30836.3151 | 0.023647 | 1.6977 | 23.731 | 27.6571 | 0.95753 | 0.086357
2025-02-07 19:43 | 0.29111 | 0.3306 | 26.4558 | 0.021773 | 0.97863 | 0.31982 | 0.00069225 | 28563.4161 | 0.023646 | 1.6978 | 22.2187 | 25.8948 | 0.8919 | 0.080438
2025-02-07 19:44 | 0.29458 | 0.33454 | 26.4561 | 0.021613 | 0.97863 | 0.32364 | 0.00070051 | 28904.4079 | 0.023646 | 1.6978 | 22.4466 | 26.1606 | 0.89542 | 0.080756
2025-02-07 19:45 | 0.29767 | 0.33805 | 26.4564 | 0.021627 | 0.97863 | 0.32703 | 0.00070786 | 29207.5169 | 0.023646 | 1.6978 | 22.6488 | 26.3965 | 0.90496 | 0.081616
2025-02-07 19:46 | 0.29805 | 0.33849 | 26.4567 | 0.021708 | 0.97863 | 0.32745 | 0.00070878 | 29245.4473 | 0.023646 | 1.6978 | 22.6741 | 26.4261 | 0.90949 | 0.082024
2025-02-07 19:47 | 0.29304 | 0.33279 | 26.457 | 0.021503 | 0.97863 | 0.32194 | 0.00069684 | 28753.0169 | 0.023646 | 1.6978 | 22.3453 | 26.0431 | 0.88645 | 0.079947
2025-02-07 19:48 | 0.3108 | 0.35296 | 26.4568 | 0.021637 | 0.97863 | 0.34145 | 0.00073907 | 30495.6009 | 0.023646 | 1.6978 | 23.5052 | 27.3948 | 0.94333 | 0.085077
2025-02-07 19:49 | 0.31466 | 0.35734 | 26.4565 | 0.021713 | 0.97863 | 0.34569 | 0.00074825 | 30874.377 | 0.023646 | 1.6978 | 23.7561 | 27.687 | 0.95784 | 0.086385
2025-02-07 19:50 | 0.29535 | 0.33542 | 26.4562 | 0.021732 | 0.97863 | 0.32448 | 0.00070235 | 28980.1949 | 0.023646 | 1.6978 | 22.4972 | 26.2196 | 0.90261 | 0.081404
2025-02-07 19:51 | 0.28531 | 0.32402 | 26.4559 | 0.021565 | 0.97863 | 0.31346 | 0.00067848 | 27995.2002 | 0.023646 | 1.6978 | 21.838 | 25.4512 | 0.86666 | 0.078162
2025-02-07 19:52 | 0.29033 | 0.32972 | 26.4556 | 0.021575 | 0.97863 | 0.31897 | 0.00069041 | 28487.6264 | 0.023646 | 1.6978 | 22.168 | 25.8356 | 0.88156 | 0.079506
2025-02-07 19:53 | 0.28763 | 0.32665 | 26.4553 | 0.021663 | 0.97863 | 0.316 | 0.00068399 | 28222.4027 | 0.023647 | 1.6977 | 21.9904 | 25.6285 | 0.87731 | 0.079122
2025-02-07 19:54 | 0.26292 | 0.29859 | 26.455 | 0.021735 | 0.97863 | 0.28886 | 0.00062523 | 25797.8844 | 0.023647 | 1.6977 | 20.3557 | 23.7231 | 0.80802 | 0.072873
2025-02-07 19:55 | 0.28377 | 0.32226 | 26.4546 | 0.021642 | 0.97863 | 0.31176 | 0.00067481 | 27843.4679 | 0.023647 | 1.6977 | 21.7363 | 25.3319 | 0.86521 | 0.078032
2025-02-07 19:56 | 0.32238 | 0.36611 | 26.4541 | 0.02162 | 0.97863 | 0.35418 | 0.00076662 | 31631.6162 | 0.023648 | 1.6977 | 24.2566 | 28.2687 | 0.97592 | 0.088016
2025-02-07 19:57 | 0.31002 | 0.35208 | 26.4536 | 0.021615 | 0.97864 | 0.3406 | 0.00073724 | 30419.311 | 0.023648 | 1.6977 | 23.4549 | 27.3342 | 0.94008 | 0.084784
2025-02-07 19:58 | 0.30616 | 0.34769 | 26.4532 | 0.02157 | 0.97864 | 0.33636 | 0.00072806 | 30040.4153 | 0.023648 | 1.6976 | 23.2035 | 27.0409 | 0.92698 | 0.083602
2025-02-07 19:59 | 0.31968 | 0.36303 | 26.4527 | 0.021506 | 0.97864 | 0.35121 | 0.00076019 | 31366.2067 | 0.023648 | 1.6976 | 24.0816 | 28.0639 | 0.96297 | 0.086848
2025-02-07 20:00 | 0.31968 | 0.36303 | 26.4523 | 0.021594 | 0.97864 | 0.35121 | 0.00076019 | 31366.1285 | 0.023649 | 1.6976 | 24.0816 | 28.0636 | 0.9669 | 0.087203
2025-02-07 20:01 | 0.32161 | 0.36523 | 26.4518 | 0.02159 | 0.97864 | 0.35333 | 0.00076478 | 31555.465 | 0.023649 | 1.6976 | 24.2066 | 28.209 | 0.97226 | 0.087686
2025-02-07 20:02 | 0.32238 | 0.3661 | 26.4522 | 0.021654 | 0.97864 | 0.35418 | 0.00076662 | 31631.2885 | 0.023649 | 1.6976 | 24.2566 | 28.2674 | 0.97741 | 0.08815
2025-02-07 20:03 | 0.30616 | 0.34769 | 26.4528 | 0.021647 | 0.97864 | 0.33636 | 0.00072806 | 30040.3585 | 0.023648 | 1.6976 | 23.2035 | 27.0407 | 0.93028 | 0.0839
2025-02-07 20:04 | 0.27952 | 0.31744 | 26.4535 | 0.02152 | 0.97864 | 0.30709 | 0.00066471 | 27426.6024 | 0.023648 | 1.6977 | 21.4563 | 25.0049 | 0.84804 | 0.076483
2025-02-07 20:05 | 0.28223 | 0.32051 | 26.4541 | 0.021595 | 0.97863 | 0.31006 | 0.00067113 | 27691.8743 | 0.023648 | 1.6977 | 21.6345 | 25.213 | 0.85885 | 0.077458
2025-02-07 20:06 | 0.29921 | 0.3398 | 26.4547 | 0.02161 | 0.97863 | 0.32873 | 0.00071153 | 29358.7847 | 0.023647 | 1.6977 | 22.7498 | 26.5132 | 0.90867 | 0.081951
2025-02-07 20:07 | 0.29265 | 0.33235 | 26.4544 | 0.021772 | 0.97863 | 0.32152 | 0.00069592 | 28714.7364 | 0.023647 | 1.6977 | 22.32 | 26.012 | 0.89632 | 0.080837
2025-02-07 20:08 | 0.2718 | 0.30867 | 26.4538 | 0.021506 | 0.97864 | 0.29861 | 0.00064634 | 26669.0022 | 0.023648 | 1.6977 | 20.9455 | 24.4098 | 0.82519 | 0.074422
2025-02-07 20:09 | 0.25018 | 0.28411 | 26.4531 | 0.021552 | 0.97864 | 0.27486 | 0.00059493 | 24547.5194 | 0.023648 | 1.6976 | 19.5044 | 22.73 | 0.76415 | 0.068917
2025-02-07 20:10 | 0.25597 | 0.29069 | 26.4525 | 0.021572 | 0.97864 | 0.28122 | 0.0006087 | 25115.6609 | 0.023649 | 1.6976 | 19.8921 | 23.1815 | 0.78172 | 0.070502
2025-02-07 20:11 | 0.25829 | 0.29332 | 26.4519 | 0.021567 | 0.97864 | 0.28377 | 0.00061421 | 25342.8644 | 0.023649 | 1.6976 | 20.0468 | 23.3614 | 0.78826 | 0.071091
2025-02-07 20:12 | 0.24632 | 0.27973 | 26.4514 | 0.021521 | 0.97864 | 0.27062 | 0.00058575 | 24168.4682 | 0.023649 | 1.6976 | 19.2453 | 22.4271 | 0.75178 | 0.067801
2025-02-07 20:13 | 0.2525 | 0.28674 | 26.4509 | 0.021438 | 0.97864 | 0.2774 | 0.00060044 | 24774.5163 | 0.02365 | 1.6975 | 19.6596 | 22.9097 | 0.76675 | 0.069151
2025-02-07 20:14 | 0.28029 | 0.31831 | 26.4505 | 0.021394 | 0.97864 | 0.30794 | 0.00066654 | 27501.9228 | 0.02365 | 1.6975 | 21.5072 | 25.0625 | 0.84522 | 0.076229
2025-02-07 20:15 | 0.3023 | 0.3433 | 26.4501 | 0.021443 | 0.97864 | 0.33212 | 0.00071887 | 29661.0949 | 0.02365 | 1.6975 | 22.9516 | 26.7454 | 0.91039 | 0.082106
2025-02-07 20:16 | 0.31041 | 0.35251 | 26.4496 | 0.021583 | 0.97864 | 0.34103 | 0.00073815 | 30456.5274 | 0.023651 | 1.6975 | 23.48 | 27.3609 | 0.93967 | 0.084746
2025-02-07 20:17 | 0.29304 | 0.33277 | 26.4487 | 0.021543 | 0.97865 | 0.32194 | 0.00069684 | 28751.7301 | 0.023651 | 1.6974 | 22.3453 | 26.038 | 0.8879 | 0.080077
2025-02-07 20:18 | 0.26292 | 0.29857 | 26.4476 | 0.02155 | 0.97865 | 0.28886 | 0.00062523 | 25796.8574 | 0.023652 | 1.6974 | 20.3557 | 23.719 | 0.80099 | 0.07224
2025-02-07 20:19 | 0.2606 | 0.29594 | 26.4466 | 0.02146 | 0.97865 | 0.28631 | 0.00061972 | 25569.4234 | 0.023653 | 1.6973 | 20.2013 | 23.5385 | 0.79092 | 0.071331
2025-02-07 20:20 | 0.28416 | 0.32268 | 26.4455 | 0.021506 | 0.97865 | 0.31218 | 0.00067572 | 27879.9794 | 0.023654 | 1.6973 | 21.7617 | 25.3561 | 0.86068 | 0.077623
2025-02-07 20:21 | 0.29612 | 0.33627 | 26.4444 | 0.021484 | 0.97865 | 0.32533 | 0.00070418 | 29054.1049 | 0.023654 | 1.6972 | 22.5477 | 26.2712 | 0.8942 | 0.080646
2025-02-07 20:22 | 0.27682 | 0.31435 | 26.4437 | 0.021488 | 0.97866 | 0.30413 | 0.00065828 | 27159.9848 | 0.023655 | 1.6972 | 21.2777 | 24.791 | 0.83877 | 0.075646
2025-02-07 20:23 | 0.28029 | 0.3183 | 26.443 | 0.021543 | 0.97866 | 0.30794 | 0.00066654 | 27500.8095 | 0.023655 | 1.6972 | 21.5072 | 25.0581 | 0.85094 | 0.076744
2025-02-07 20:24 | 0.3023 | 0.34329 | 26.4424 | 0.021437 | 0.97866 | 0.33212 | 0.00071887 | 29659.8593 | 0.023656 | 1.6972 | 22.9516 | 26.7405 | 0.90993 | 0.082064
2025-02-07 20:25 | 0.31427 | 0.35688 | 26.4418 | 0.021358 | 0.97866 | 0.34527 | 0.00074734 | 30834.024 | 0.023656 | 1.6971 | 23.731 | 27.6481 | 0.94066 | 0.084836
2025-02-07 20:26 | 0.31388 | 0.35644 | 26.4411 | 0.021389 | 0.97866 | 0.34484 | 0.00074642 | 30796.0386 | 0.023657 | 1.6971 | 23.7059 | 27.6185 | 0.94091 | 0.084858
2025-02-07 20:27 | 0.2884 | 0.3275 | 26.4406 | 0.021267 | 0.97866 | 0.31685 | 0.00068582 | 28295.9165 | 0.023657 | 1.6971 | 22.0412 | 25.6787 | 0.86311 | 0.077842
2025-02-07 20:28 | 0.27759 | 0.31522 | 26.4402 | 0.021477 | 0.97866 | 0.30497 | 0.00066012 | 27235.2301 | 0.023657 | 1.6971 | 21.3288 | 24.8485 | 0.84047 | 0.0758
2025-02-07 20:29 | 0.29265 | 0.33232 | 26.4398 | 0.021242 | 0.97866 | 0.32152 | 0.00069592 | 28712.4569 | 0.023658 | 1.697 | 22.32 | 26.003 | 0.87414 | 0.078837
2025-02-07 20:30 | 0.28531 | 0.32399 | 26.4393 | 0.021191 | 0.97866 | 0.31346 | 0.00067848 | 27992.6859 | 0.023658 | 1.697 | 21.838 | 25.4412 | 0.85121 | 0.076769
2025-02-07 20:31 | 0.27489 | 0.31215 | 26.4389 | 0.021219 | 0.97867 | 0.302 | 0.00065369 | 26969.8794 | 0.023658 | 1.697 | 21.1501 | 24.6395 | 0.82263 | 0.074191
2025-02-07 20:32 | 0.25636 | 0.29111 | 26.4376 | 0.021359 | 0.97867 | 0.28164 | 0.00060962 | 25151.5167 | 0.023659 | 1.6969 | 19.9179 | 23.2033 | 0.77475 | 0.069873
2025-02-07 20:33 | 0.26292 | 0.29856 | 26.4361 | 0.021162 | 0.97867 | 0.28886 | 0.00062523 | 25795.2464 | 0.02366 | 1.6969 | 20.3557 | 23.7125 | 0.78631 | 0.070916
2025-02-07 20:34 | 0.29497 | 0.33494 | 26.4346 | 0.021239 | 0.97867 | 0.32406 | 0.00070143 | 28938.9239 | 0.023661 | 1.6968 | 22.4719 | 26.1767 | 0.88046 | 0.079407
2025-02-07 20:35 | 0.31157 | 0.35379 | 26.4331 | 0.021138 | 0.97868 | 0.3423 | 0.00074091 | 30567.4371 | 0.023662 | 1.6967 | 23.5554 | 27.4379 | 0.92312 | 0.083254
2025-02-07 20:36 | 0.31388 | 0.35642 | 26.4318 | 0.021236 | 0.97868 | 0.34484 | 0.00074642 | 30794.4809 | 0.023663 | 1.6967 | 23.7059 | 27.6124 | 0.93394 | 0.08423
2025-02-07 20:37 | 0.31157 | 0.35379 | 26.433 | 0.021357 | 0.97868 | 0.3423 | 0.00074091 | 30567.4238 | 0.023662 | 1.6967 | 23.5554 | 27.4378 | 0.93269 | 0.084117
2025-02-07 20:38 | 0.3274 | 0.37177 | 26.4352 | 0.021324 | 0.97867 | 0.35969 | 0.00077855 | 32120.7911 | 0.023661 | 1.6968 | 24.581 | 28.634 | 0.97625 | 0.088046
2025-02-07 20:39 | 0.32662 | 0.3709 | 26.4373 | 0.021204 | 0.97867 | 0.35884 | 0.00077671 | 32045.408 | 0.023659 | 1.6969 | 24.5311 | 28.5773 | 0.96867 | 0.087362
2025-02-07 20:40 | 0.31427 | 0.35687 | 26.4395 | 0.021167 | 0.97866 | 0.34527 | 0.00074734 | 30833.6478 | 0.023658 | 1.697 | 23.731 | 27.6466 | 0.9322 | 0.084073
2025-02-07 20:41 | 0.30423 | 0.34548 | 26.4415 | 0.021251 | 0.97866 | 0.33424 | 0.00072346 | 29849.1154 | 0.023656 | 1.6971 | 23.0776 | 26.8868 | 0.90746 | 0.081842
2025-02-07 20:42 | 0.28647 | 0.32531 | 26.4415 | 0.021167 | 0.97866 | 0.31473 | 0.00068123 | 28106.6558 | 0.023656 | 1.6971 | 21.9142 | 25.5313 | 0.85359 | 0.076984
2025-02-07 20:43 | 0.30539 | 0.34679 | 26.4409 | 0.021179 | 0.97866 | 0.33551 | 0.00072622 | 29962.6515 | 0.023657 | 1.6971 | 23.1532 | 26.9744 | 0.90767 | 0.08186
2025-02-07 20:44 | 0.31659 | 0.3595 | 26.4402 | 0.021173 | 0.97866 | 0.34781 | 0.00075284 | 31061.0468 | 0.023657 | 1.6971 | 23.8813 | 27.8223 | 0.93902 | 0.084688
2025-02-07 20:45 | 0.30771 | 0.34942 | 26.4396 | 0.02131 | 0.97866 | 0.33806 | 0.00073173 | 30189.7166 | 0.023658 | 1.697 | 23.3041 | 27.1494 | 0.91984 | 0.082958
2025-02-07 20:46 | 0.31234 | 0.35468 | 26.4389 | 0.021328 | 0.97867 | 0.34315 | 0.00074274 | 30644.1444 | 0.023658 | 1.697 | 23.6056 | 27.5001 | 0.93378 | 0.084215
2025-02-07 20:47 | 0.30925 | 0.35117 | 26.4367 | 0.021268 | 0.97867 | 0.33975 | 0.0007354 | 30340.7634 | 0.02366 | 1.6969 | 23.4047 | 27.2647 | 0.92235 | 0.083184
2025-02-07 20:48 | 0.31659 | 0.35949 | 26.4342 | 0.021131 | 0.97868 | 0.34781 | 0.00075284 | 31060.0233 | 0.023662 | 1.6968 | 23.8813 | 27.8183 | 0.937 | 0.084506
2025-02-07 20:49 | 0.33049 | 0.37527 | 26.4316 | 0.021167 | 0.97868 | 0.36308 | 0.0007859 | 32423.1819 | 0.023663 | 1.6967 | 24.7803 | 28.8636 | 0.97767 | 0.088174
2025-02-07 20:50 | 0.31388 | 0.35641 | 26.429 | 0.021125 | 0.97869 | 0.34484 | 0.00074642 | 30794.017 | 0.023665 | 1.6966 | 23.7059 | 27.6105 | 0.92899 | 0.083783
2025-02-07 20:51 | 0.31157 | 0.35378 | 26.4267 | 0.021209 | 0.97869 | 0.3423 | 0.00074091 | 30566.3691 | 0.023667 | 1.6965 | 23.5554 | 27.4337 | 0.92605 | 0.083518
2025-02-07 20:52 | 0.32547 | 0.36956 | 26.4279 | 0.021149 | 0.97869 | 0.35757 | 0.00077396 | 31930.1337 | 0.023666 | 1.6965 | 24.4563 | 28.4838 | 0.96263 | 0.086817
2025-02-07 20:53 | 0.32006 | 0.36343 | 26.4302 | 0.021102 | 0.97868 | 0.35163 | 0.00076111 | 31400.2599 | 0.023664 | 1.6966 | 24.1066 | 28.078 | 0.94534 | 0.085258
2025-02-07 20:54 | 0.30307 | 0.34414 | 26.4326 | 0.02109 | 0.97868 | 0.33297 | 0.00072071 | 29734.0404 | 0.023663 | 1.6967 | 23.0021 | 26.7931 | 0.89709 | 0.080907
2025-02-07 20:55 | 0.28261 | 0.32091 | 26.435 | 0.021066 | 0.97867 | 0.31049 | 0.00067205 | 27726.874 | 0.023661 | 1.6968 | 21.66 | 25.2312 | 0.83844 | 0.075617
2025-02-07 20:56 | 0.26562 | 0.30163 | 26.4372 | 0.021107 | 0.97867 | 0.29182 | 0.00063165 | 26060.5495 | 0.023659 | 1.6969 | 20.5355 | 23.9226 | 0.79197 | 0.071426
2025-02-07 20:57 | 0.28531 | 0.32399 | 26.4379 | 0.020994 | 0.97867 | 0.31346 | 0.00067848 | 27992.4715 | 0.023659 | 1.697 | 21.838 | 25.4404 | 0.84327 | 0.076053
2025-02-07 20:58 | 0.27875 | 0.31653 | 26.4381 | 0.021073 | 0.97867 | 0.30625 | 0.00066287 | 27348.5636 | 0.023659 | 1.697 | 21.4053 | 24.9364 | 0.82787 | 0.074664
2025-02-07 20:59 | 0.29844 | 0.33889 | 26.4384 | 0.021053 | 0.97867 | 0.32788 | 0.00070969 | 29280.4215 | 0.023659 | 1.697 | 22.6993 | 26.444 | 0.88267 | 0.079606
2025-02-07 21:00 | 0.31234 | 0.35468 | 26.4386 | 0.021067 | 0.97867 | 0.34315 | 0.00074274 | 30644.0986 | 0.023658 | 1.697 | 23.6056 | 27.4999 | 0.92234 | 0.083184
2025-02-07 21:01 | 0.29033 | 0.32969 | 26.4388 | 0.021149 | 0.97867 | 0.31897 | 0.00069041 | 28485.0282 | 0.023658 | 1.697 | 22.168 | 25.8253 | 0.86373 | 0.077898
2025-02-07 21:02 | 0.30307 | 0.34416 | 26.4388 | 0.021061 | 0.97867 | 0.33297 | 0.00072071 | 29735.0439 | 0.023658 | 1.697 | 23.0021 | 26.797 | 0.89602 | 0.08081
2025-02-07 21:03 | 0.30385 | 0.34503 | 26.4388 | 0.021228 | 0.97867 | 0.33382 | 0.00072255 | 29810.8019 | 0.023658 | 1.697 | 23.0524 | 26.8557 | 0.90531 | 0.081648
2025-02-07 21:04 | 0.29728 | 0.33758 | 26.4388 | 0.021112 | 0.97867 | 0.32661 | 0.00070694 | 29166.8589 | 0.023658 | 1.697 | 22.6236 | 26.3561 | 0.88184 | 0.079531
2025-02-07 21:05 | 0.29188 | 0.33144 | 26.4388 | 0.02106 | 0.97867 | 0.32067 | 0.00069409 | 28636.5529 | 0.023658 | 1.697 | 22.2693 | 25.9434 | 0.86445 | 0.077963
2025-02-07 21:06 | 0.29574 | 0.33583 | 26.4388 | 0.021084 | 0.97867 | 0.32491 | 0.00070327 | 29015.3429 | 0.023658 | 1.697 | 22.5224 | 26.2383 | 0.87632 | 0.079033
2025-02-07 21:07 | 0.30307 | 0.34416 | 26.4388 | 0.021034 | 0.97867 | 0.33297 | 0.00072071 | 29735.0439 | 0.023658 | 1.697 | 23.0021 | 26.797 | 0.8949 | 0.080709
2025-02-07 21:08 | 0.29805 | 0.33846 | 26.4388 | 0.020941 | 0.97867 | 0.32745 | 0.00070878 | 29242.6066 | 0.023658 | 1.697 | 22.6741 | 26.4149 | 0.87686 | 0.079082
2025-02-07 21:09 | 0.29111 | 0.33056 | 26.4379 | 0.021012 | 0.97867 | 0.31982 | 0.00069225 | 28560.6552 | 0.023659 | 1.697 | 22.2187 | 25.8838 | 0.8603 | 0.077588
2025-02-07 21:10 | 0.29844 | 0.33889 | 26.4369 | 0.020941 | 0.97867 | 0.32788 | 0.00070969 | 29280.1837 | 0.02366 | 1.6969 | 22.6993 | 26.4431 | 0.8779 | 0.079175
2025-02-07 21:11 | 0.30886 | 0.35073 | 26.4358 | 0.021031 | 0.97867 | 0.33933 | 0.00073448 | 30302.7305 | 0.02366 | 1.6969 | 23.3795 | 27.2348 | 0.91095 | 0.082157
2025-02-07 21:12 | 0.32161 | 0.36519 | 26.4347 | 0.021054 | 0.97867 | 0.35333 | 0.00076478 | 31552.5347 | 0.023661 | 1.6968 | 24.2066 | 28.1975 | 0.94768 | 0.085469
2025-02-07 21:13 | 0.31852 | 0.36168 | 26.4337 | 0.021058 | 0.97868 | 0.34993 | 0.00075743 | 31249.3308 | 0.023662 | 1.6968 | 24.0065 | 27.9638 | 0.93917 | 0.084701
2025-02-07 21:14 | 0.32392 | 0.36782 | 26.4329 | 0.020891 | 0.97868 | 0.35587 | 0.00077029 | 31779.495 | 0.023662 | 1.6967 | 24.3565 | 28.3709 | 0.94674 | 0.085384
2025-02-07 21:15 | 0.33512 | 0.38053 | 26.4323 | 0.02092 | 0.97868 | 0.36817 | 0.00079691 | 32877.8374 | 0.023663 | 1.6967 | 25.0787 | 29.2118 | 0.97915 | 0.088307
2025-02-07 21:16 | 0.32431 | 0.36825 | 26.4316 | 0.021032 | 0.97868 | 0.3563 | 0.00077121 | 31817.1504 | 0.023663 | 1.6967 | 24.3814 | 28.3991 | 0.95417 | 0.086055
2025-02-07 21:17 | 0.32431 | 0.36825 | 26.431 | 0.021082 | 0.97868 | 0.3563 | 0.00077121 | 31817.0391 | 0.023664 | 1.6966 | 24.3814 | 28.3987 | 0.95639 | 0.086255
2025-02-07 21:18 | 0.30693 | 0.34852 | 26.4304 | 0.021227 | 0.97868 | 0.33721 | 0.00072989 | 30112.4584 | 0.023664 | 1.6966 | 23.2538 | 27.0849 | 0.91381 | 0.082414
2025-02-07 21:19 | 0.28647 | 0.32529 | 26.4305 | 0.021101 | 0.97868 | 0.31473 | 0.00068123 | 28104.9729 | 0.023664 | 1.6966 | 21.9142 | 25.5246 | 0.85064 | 0.076718
2025-02-07 21:20 | 0.30925 | 0.35115 | 26.4307 | 0.021191 | 0.97868 | 0.33975 | 0.0007354 | 30339.779 | 0.023664 | 1.6966 | 23.4047 | 27.2608 | 0.91883 | 0.082867
2025-02-07 21:21 | 0.32971 | 0.37439 | 26.431 | 0.021129 | 0.97868 | 0.36224 | 0.00078406 | 32347.3263 | 0.023664 | 1.6966 | 24.7305 | 28.8052 | 0.97374 | 0.08782
2025-02-07 21:22 | 0.32045 | 0.36387 | 26.4313 | 0.02137 | 0.97868 | 0.35206 | 0.00076203 | 31438.3117 | 0.023664 | 1.6967 | 24.1316 | 28.1078 | 0.95849 | 0.086444
2025-02-07 21:23 | 0.32083 | 0.36431 | 26.4313 | 0.021115 | 0.97868 | 0.35248 | 0.00076294 | 31476.1988 | 0.023664 | 1.6967 | 24.1566 | 28.137 | 0.94813 | 0.08551
2025-02-07 21:24 | 0.31543 | 0.35817 | 26.4313 | 0.021162 | 0.97868 | 0.34654 | 0.00075009 | 30945.9134 | 0.023664 | 1.6967 | 23.8062 | 27.7289 | 0.93502 | 0.084327
2025-02-07 21:25 | 0.29458 | 0.3345 | 26.4313 | 0.021119 | 0.97868 | 0.32364 | 0.00070051 | 28900.5294 | 0.023664 | 1.6967 | 22.4466 | 26.1452 | 0.87435 | 0.078855
2025-02-07 21:26 | 0.28416 | 0.32266 | 26.4313 | 0.02116 | 0.97868 | 0.31218 | 0.00067572 | 27877.8371 | 0.023664 | 1.6967 | 21.7617 | 25.3475 | 0.8465 | 0.076344
2025-02-07 21:27 | 0.28493 | 0.32354 | 26.4313 | 0.021057 | 0.97868 | 0.31303 | 0.00067756 | 27953.5916 | 0.023664 | 1.6967 | 21.8126 | 25.4068 | 0.84453 | 0.076166
2025-02-07 21:28 | 0.30307 | 0.34414 | 26.4313 | 0.021053 | 0.97868 | 0.33297 | 0.00072071 | 29733.8335 | 0.023664 | 1.6967 | 23.0021 | 26.7922 | 0.89549 | 0.080762
2025-02-07 21:29 | 0.31157 | 0.35379 | 26.4313 | 0.021257 | 0.97868 | 0.3423 | 0.00074091 | 30567.1314 | 0.023664 | 1.6967 | 23.5554 | 27.4367 | 0.92829 | 0.08372
2025-02-07 21:30 | 0.31968 | 0.36299 | 26.4308 | 0.021065 | 0.97868 | 0.35121 | 0.00076019 | 31362.4716 | 0.023664 | 1.6966 | 24.0816 | 28.0493 | 0.94265 | 0.085016
2025-02-07 21:31 | 0.31002 | 0.35203 | 26.4301 | 0.020949 | 0.97868 | 0.3406 | 0.00073724 | 30415.431 | 0.023664 | 1.6966 | 23.4549 | 27.319 | 0.91048 | 0.082114
2025-02-07 21:32 | 0.28493 | 0.32353 | 26.4295 | 0.020867 | 0.97868 | 0.31303 | 0.00067756 | 27953.3125 | 0.023665 | 1.6966 | 21.8126 | 25.4057 | 0.83687 | 0.075476
2025-02-07 21:33 | 0.30346 | 0.34458 | 26.4288 | 0.020871 | 0.97869 | 0.33339 | 0.00072163 | 29771.31 | 0.023665 | 1.6965 | 23.0273 | 26.82 | 0.88879 | 0.080158
2025-02-07 21:34 | 0.34438 | 0.39104 | 26.4282 | 0.020957 | 0.97869 | 0.37835 | 0.00081895 | 33786.149 | 0.023666 | 1.6965 | 25.6739 | 29.9021 | 1.0066 | 0.090779
2025-02-07 21:35 | 0.32585 | 0.37 | 26.4274 | 0.02101 | 0.97869 | 0.35799 | 0.00077488 | 31967.9194 | 0.023666 | 1.6965 | 24.4812 | 28.5125 | 0.95734 | 0.086341
2025-02-07 21:36 | 0.32469 | 0.36868 | 26.4265 | 0.020905 | 0.97869 | 0.35672 | 0.00077212 | 31854.1422 | 0.023667 | 1.6964 | 24.4064 | 28.4247 | 0.94932 | 0.085617
2025-02-07 21:37 | 0.34593 | 0.39279 | 26.4256 | 0.021029 | 0.97869 | 0.38005 | 0.00082262 | 33937.1915 | 0.023668 | 1.6964 | 25.7729 | 30.0156 | 1.0142 | 0.09147
2025-02-07 21:38 | 0.34902 | 0.3963 | 26.4248 | 0.021084 | 0.97869 | 0.38344 | 0.00082996 | 34240.0426 | 0.023668 | 1.6964 | 25.9707 | 30.2453 | 1.0255 | 0.092484
2025-02-07 21:39 | 0.33821 | 0.38402 | 26.4239 | 0.021255 | 0.9787 | 0.37157 | 0.00080426 | 33179.3596 | 0.023669 | 1.6963 | 25.2774 | 29.4373 | 1.0033 | 0.090487
2025-02-07 21:40 | 0.344 | 0.39059 | 26.4233 | 0.021215 | 0.9787 | 0.37793 | 0.00081803 | 33747.3731 | 0.023669 | 1.6963 | 25.6492 | 29.8698 | 1.0177 | 0.091783
2025-02-07 21:41 | 0.34052 | 0.38665 | 26.4226 | 0.021053 | 0.9787 | 0.37411 | 0.00080977 | 33406.3734 | 0.02367 | 1.6963 | 25.4262 | 29.6097 | 1.0002 | 0.090205
2025-02-07 21:42 | 0.33975 | 0.38577 | 26.422 | 0.020976 | 0.9787 | 0.37326 | 0.00080793 | 33330.5063 | 0.02367 | 1.6962 | 25.3766 | 29.5515 | 0.9944 | 0.089682
2025-02-07 21:43 | 0.36137 | 0.41032 | 26.4213 | 0.02106 | 0.9787 | 0.39702 | 0.00085934 | 35451.4154 | 0.023671 | 1.6962 | 26.7594 | 31.1613 | 1.0586 | 0.095476
2025-02-07 21:44 | 0.3633 | 0.41251 | 26.4207 | 0.021148 | 0.9787 | 0.39914 | 0.00086393 | 35640.6791 | 0.023671 | 1.6962 | 26.8823 | 31.3039 | 1.0684 | 0.096361
2025-02-07 21:45 | 0.36214 | 0.41119 | 26.4208 | 0.021048 | 0.9787 | 0.39787 | 0.00086118 | 35527.0606 | 0.023671 | 1.6962 | 26.8085 | 31.2181 | 1.0602 | 0.095614
2025-02-07 21:46 | 0.34709 | 0.3941 | 26.421 | 0.02115 | 0.9787 | 0.38132 | 0.00082537 | 34049.9616 | 0.023671 | 1.6962 | 25.8471 | 30.0987 | 1.0232 | 0.092279
2025-02-07 21:47 | 0.32778 | 0.37218 | 26.4212 | 0.021048 | 0.9787 | 0.36011 | 0.00077947 | 32156.2308 | 0.023671 | 1.6962 | 24.6059 | 28.6535 | 0.96431 | 0.086969
2025-02-07 21:48 | 0.31388 | 0.3564 | 26.4214 | 0.020941 | 0.9787 | 0.34484 | 0.00074642 | 30792.7519 | 0.023671 | 1.6962 | 23.7059 | 27.6056 | 0.92066 | 0.083032
2025-02-07 21:49 | 0.29998 | 0.34062 | 26.4215 | 0.020831 | 0.9787 | 0.32957 | 0.00071337 | 29429.2558 | 0.02367 | 1.6962 | 22.8003 | 26.5511 | 0.87721 | 0.079113
2025-02-07 21:50 | 0.29574 | 0.33579 | 26.4207 | 0.02086 | 0.9787 | 0.32491 | 0.00070327 | 29012.4971 | 0.023671 | 1.6962 | 22.5224 | 26.227 | 0.86655 | 0.078152
2025-02-07 21:51 | 0.31659 | 0.35946 | 26.4197 | 0.020893 | 0.9787 | 0.34781 | 0.00075284 | 31057.5832 | 0.023672 | 1.6961 | 23.8813 | 27.8087 | 0.92604 | 0.083518
2025-02-07 21:52 | 0.33242 | 0.37743 | 26.4186 | 0.020891 | 0.97871 | 0.3652 | 0.00079049 | 32610.2722 | 0.023673 | 1.6961 | 24.9047 | 28.9996 | 0.96989 | 0.087472
2025-02-07 21:53 | 0.31852 | 0.36165 | 26.4175 | 0.021029 | 0.97871 | 0.34993 | 0.00075743 | 31246.5934 | 0.023673 | 1.696 | 24.0065 | 27.953 | 0.93741 | 0.084543
2025-02-07 21:54 | 0.3162 | 0.35902 | 26.4166 | 0.021025 | 0.97871 | 0.34739 | 0.00075193 | 31019.1904 | 0.023674 | 1.696 | 23.8563 | 27.7775 | 0.93074 | 0.083941
2025-02-07 21:55 | 0.32624 | 0.37042 | 26.4172 | 0.020926 | 0.97871 | 0.35842 | 0.0007758 | 32004.0426 | 0.023674 | 1.696 | 24.5062 | 28.5347 | 0.9543 | 0.086066
2025-02-07 21:56 | 0.31929 | 0.36253 | 26.4183 | 0.020971 | 0.97871 | 0.35078 | 0.00075927 | 31322.4816 | 0.023673 | 1.6961 | 24.0566 | 28.0119 | 0.93701 | 0.084506
2025-02-07 21:57 | 0.31929 | 0.36253 | 26.4194 | 0.02109 | 0.97871 | 0.35078 | 0.00075927 | 31322.6642 | 0.023672 | 1.6961 | 24.0566 | 28.0126 | 0.94236 | 0.084989
2025-02-07 21:58 | 0.33049 | 0.37525 | 26.4205 | 0.021169 | 0.9787 | 0.36308 | 0.0007859 | 32421.2297 | 0.023671 | 1.6962 | 24.7803 | 28.856 | 0.97745 | 0.088154
2025-02-07 21:59 | 0.31195 | 0.35421 | 26.4214 | 0.021271 | 0.9787 | 0.34272 | 0.00074183 | 30603.3712 | 0.023671 | 1.6962 | 23.5805 | 27.4595 | 0.92972 | 0.08385
2025-02-07 22:00 | 0.305 | 0.34631 | 26.4209 | 0.021089 | 0.9787 | 0.33509 | 0.0007253 | 29921.5323 | 0.023671 | 1.6962 | 23.128 | 26.9323 | 0.90221 | 0.081368
2025-02-07 22:01 | 0.30848 | 0.35026 | 26.42 | 0.021135 | 0.9787 | 0.33891 | 0.00073356 | 30262.2695 | 0.023672 | 1.6962 | 23.3544 | 27.1954 | 0.91392 | 0.082424
2025-02-07 22:02 | 0.3135 | 0.35595 | 26.4192 | 0.021151 | 0.97871 | 0.34442 | 0.0007455 | 30754.5043 | 0.023672 | 1.6961 | 23.6808 | 27.5749 | 0.92876 | 0.083762
2025-02-07 22:03 | 0.31466 | 0.35727 | 26.4183 | 0.021134 | 0.97871 | 0.34569 | 0.00074825 | 30867.986 | 0.023673 | 1.6961 | 23.7561 | 27.662 | 0.93124 | 0.083987
2025-02-07 22:04 | 0.305 | 0.34631 | 26.4175 | 0.020903 | 0.97871 | 0.33509 | 0.0007253 | 29920.9783 | 0.023673 | 1.696 | 23.128 | 26.9301 | 0.89414 | 0.080641
2025-02-07 22:05 | 0.3162 | 0.35902 | 26.4168 | 0.020951 | 0.97871 | 0.34739 | 0.00075193 | 31019.2281 | 0.023674 | 1.696 | 23.8563 | 27.7777 | 0.92748 | 0.083647
2025-02-07 22:06 | 0.33782 | 0.38357 | 26.4162 | 0.021003 | 0.97871 | 0.37114 | 0.00080334 | 33140.0855 | 0.023674 | 1.696 | 25.2526 | 29.403 | 0.99013 | 0.089298
2025-02-07 22:07 | 0.35095 | 0.39847 | 26.4155 | 0.021036 | 0.97871 | 0.38556 | 0.00083456 | 34427.6945 | 0.023675 | 1.6959 | 26.0942 | 30.3825 | 1.0283 | 0.092735
2025-02-07 22:08 | 0.35635 | 0.4046 | 26.4149 | 0.02099 | 0.97871 | 0.3915 | 0.00084741 | 34957.8134 | 0.023675 | 1.6959 | 26.4394 | 30.784 | 1.041 | 0.093883
2025-02-07 22:09 | 0.36562 | 0.41512 | 26.4142 | 0.020966 | 0.97872 | 0.40168 | 0.00086944 | 35866.6696 | 0.023676 | 1.6959 | 27.0296 | 31.4707 | 1.0655 | 0.096094
2025-02-07 22:10 | 0.35404 | 0.40197 | 26.4137 | 0.021178 | 0.97872 | 0.38896 | 0.0008419 | 34730.3552 | 0.023676 | 1.6959 | 26.2916 | 30.611 | 1.0438 | 0.094137
2025-02-07 22:11 | 0.3413 | 0.38751 | 26.4133 | 0.021065 | 0.97872 | 0.37496 | 0.0008116 | 33480.4336 | 0.023676 | 1.6958 | 25.4758 | 29.6609 | 1.0027 | 0.090429
2025-02-07 22:12 | 0.33512 | 0.38049 | 26.4128 | 0.021002 | 0.97872 | 0.36817 | 0.00079691 | 32874.3711 | 0.023677 | 1.6958 | 25.0787 | 29.1983 | 0.98243 | 0.088603
2025-02-07 22:13 | 0.33164 | 0.37654 | 26.4124 | 0.020826 | 0.97872 | 0.36436 | 0.00078865 | 32533.4263 | 0.023677 | 1.6958 | 24.8549 | 28.9374 | 0.96457 | 0.086993
2025-02-07 22:14 | 0.30037 | 0.34104 | 26.4119 | 0.020988 | 0.97872 | 0.33 | 0.00071428 | 29465.5912 | 0.023677 | 1.6958 | 22.8255 | 26.5744 | 0.88467 | 0.079786
2025-02-07 22:15 | 0.32315 | 0.3669 | 26.4114 | 0.02102 | 0.97872 | 0.35502 | 0.00076845 | 31700.0488 | 0.023678 | 1.6958 | 24.3065 | 28.2983 | 0.94982 | 0.085662
2025-02-07 22:16 | 0.33589 | 0.38136 | 26.411 | 0.020941 | 0.97872 | 0.36902 | 0.00079875 | 32949.7919 | 0.023678 | 1.6957 | 25.1284 | 29.2549 | 0.98166 | 0.088534
2025-02-07 22:17 | 0.33319 | 0.37829 | 26.4107 | 0.02102 | 0.97872 | 0.36605 | 0.00079232 | 32684.6194 | 0.023678 | 1.6957 | 24.9545 | 29.0521 | 0.97784 | 0.088189
2025-02-07 22:18 | 0.33859 | 0.38443 | 26.4104 | 0.020968 | 0.97872 | 0.37199 | 0.00080518 | 33214.7897 | 0.023678 | 1.6957 | 25.3022 | 29.4567 | 0.99047 | 0.089328
2025-02-07 22:19 | 0.33319 | 0.37829 | 26.41 | 0.020988 | 0.97872 | 0.36605 | 0.00079232 | 32684.5108 | 0.023679 | 1.6957 | 24.9545 | 29.0517 | 0.97634 | 0.088054
2025-02-07 22:20 | 0.34631 | 0.3932 | 26.4097 | 0.021012 | 0.97872 | 0.38047 | 0.00082354 | 33972.1408 | 0.023679 | 1.6957 | 25.7977 | 30.0331 | 1.014 | 0.091452
2025-02-07 22:21 | 0.33821 | 0.38399 | 26.4094 | 0.021259 | 0.97873 | 0.37157 | 0.00080426 | 33176.7521 | 0.023679 | 1.6957 | 25.2774 | 29.4272 | 1.0031 | 0.090463
2025-02-07 22:22 | 0.32276 | 0.36646 | 26.4091 | 0.021231 | 0.97873 | 0.3546 | 0.00076753 | 31661.779 | 0.023679 | 1.6957 | 24.2815 | 28.2677 | 0.95818 | 0.086416
2025-02-07 22:23 | 0.31466 | 0.35725 | 26.4089 | 0.020941 | 0.97873 | 0.34569 | 0.00074825 | 30866.4075 | 0.023679 | 1.6957 | 23.7561 | 27.6558 | 0.92248 | 0.083196
2025-02-07 22:24 | 0.32971 | 0.37435 | 26.4094 | 0.020758 | 0.97873 | 0.36224 | 0.00078406 | 32343.5334 | 0.023679 | 1.6957 | 24.7305 | 28.7905 | 0.95602 | 0.086221
2025-02-07 22:25 | 0.3301 | 0.37479 | 26.41 | 0.020877 | 0.97872 | 0.36266 | 0.00078498 | 32381.5201 | 0.023679 | 1.6957 | 24.7554 | 28.8199 | 0.9626 | 0.086815
2025-02-07 22:26 | 0.33821 | 0.38399 | 26.4107 | 0.021024 | 0.97872 | 0.37157 | 0.00080426 | 33176.9718 | 0.023678 | 1.6957 | 25.2774 | 29.4281 | 0.99203 | 0.089468
2025-02-07 22:27 | 0.33242 | 0.37742 | 26.4113 | 0.021004 | 0.97872 | 0.3652 | 0.00079049 | 32608.9863 | 0.023678 | 1.6958 | 24.9047 | 28.9946 | 0.97496 | 0.087929
2025-02-07 22:28 | 0.32045 | 0.36383 | 26.4118 | 0.021008 | 0.97872 | 0.35206 | 0.00076203 | 31435.0037 | 0.023677 | 1.6958 | 24.1316 | 28.0949 | 0.94174 | 0.084933
2025-02-07 22:29 | 0.30925 | 0.35112 | 26.4114 | 0.021044 | 0.97872 | 0.33975 | 0.0007354 | 30336.604 | 0.023678 | 1.6958 | 23.4047 | 27.2483 | 0.91194 | 0.082246
2025-02-07 22:30 | 0.29535 | 0.33534 | 26.4108 | 0.021064 | 0.97872 | 0.32448 | 0.00070235 | 28973.0589 | 0.023678 | 1.6957 | 22.4972 | 26.1914 | 0.87371 | 0.078798
2025-02-07 22:31 | 0.31041 | 0.35243 | 26.4101 | 0.021127 | 0.97872 | 0.34103 | 0.00073815 | 30450.0104 | 0.023679 | 1.6957 | 23.48 | 27.3352 | 0.91878 | 0.082863
2025-02-07 22:32 | 0.34284 | 0.38925 | 26.4095 | 0.021091 | 0.97873 | 0.37666 | 0.00081528 | 33631.2379 | 0.023679 | 1.6957 | 25.5749 | 29.7736 | 1.0081 | 0.090918
2025-02-07 22:33 | 0.33319 | 0.37829 | 26.4089 | 0.021052 | 0.97873 | 0.36605 | 0.00079232 | 32684.3109 | 0.023679 | 1.6957 | 24.9545 | 29.0509 | 0.97925 | 0.088317
2025-02-07 22:34 | 0.30809 | 0.3498 | 26.409 | 0.021039 | 0.97873 | 0.33848 | 0.00073265 | 30222.5844 | 0.023679 | 1.6957 | 23.3293 | 27.159 | 0.90843 | 0.081929
2025-02-07 22:35 | 0.28802 | 0.327 | 26.4092 | 0.021012 | 0.97873 | 0.31643 | 0.0006849 | 28253.2255 | 0.023679 | 1.6957 | 22.0158 | 25.63 | 0.8509 | 0.076741
2025-02-07 22:36 | 0.28647 | 0.32525 | 26.4094 | 0.021027 | 0.97873 | 0.31473 | 0.00068123 | 28101.7661 | 0.023679 | 1.6957 | 21.9142 | 25.5119 | 0.84716 | 0.076403
2025-02-07 22:37 | 0.28995 | 0.3292 | 26.4096 | 0.020994 | 0.97872 | 0.31855 | 0.0006895 | 28442.6561 | 0.023679 | 1.6957 | 22.1426 | 25.7779 | 0.85559 | 0.077163
2025-02-07 22:38 | 0.30076 | 0.34147 | 26.4098 | 0.021095 | 0.97872 | 0.33042 | 0.0007152 | 29503.1262 | 0.023679 | 1.6957 | 22.8508 | 26.6024 | 0.89018 | 0.080283
2025-02-07 22:39 | 0.32161 | 0.36514 | 26.4094 | 0.020984 | 0.97873 | 0.35333 | 0.00076478 | 31548.2135 | 0.023679 | 1.6957 | 24.2066 | 28.1806 | 0.94384 | 0.085122
2025-02-07 22:40 | 0.33203 | 0.37698 | 26.409 | 0.021041 | 0.97873 | 0.36478 | 0.00078957 | 32570.7035 | 0.023679 | 1.6957 | 24.8798 | 28.9641 | 0.9755 | 0.087978
2025-02-07 22:41 | 0.34284 | 0.38925 | 26.4085 | 0.021073 | 0.97873 | 0.37666 | 0.00081528 | 33631.0615 | 0.02368 | 1.6956 | 25.5749 | 29.7729 | 1.0072 | 0.09084
2025-02-07 22:42 | 0.34477 | 0.39144 | 26.4081 | 0.02118 | 0.97873 | 0.37878 | 0.00081987 | 33820.3412 | 0.02368 | 1.6956 | 25.6987 | 29.9167 | 1.0177 | 0.091787
2025-02-07 22:43 | 0.34361 | 0.39012 | 26.4076 | 0.021174 | 0.97873 | 0.37751 | 0.00081711 | 33706.6392 | 0.02368 | 1.6956 | 25.6244 | 29.8299 | 1.0142 | 0.091467
2025-02-07 22:44 | 0.33242 | 0.37741 | 26.4071 | 0.021137 | 0.97873 | 0.3652 | 0.00079049 | 32608.2519 | 0.023681 | 1.6956 | 24.9047 | 28.9918 | 0.981 | 0.088474
2025-02-07 22:45 | 0.3108 | 0.35286 | 26.4067 | 0.021212 | 0.97873 | 0.34145 | 0.00073907 | 30487.3144 | 0.023681 | 1.6956 | 23.5052 | 27.3622 | 0.92347 | 0.083286
2025-02-07 22:46 | 0.30153 | 0.34234 | 26.4062 | 0.020987 | 0.97873 | 0.33127 | 0.00071704 | 29578.3068 | 0.023681 | 1.6955 | 22.9012 | 26.6589 | 0.88771 | 0.080061
2025-02-07 22:47 | 0.33049 | 0.37522 | 26.4058 | 0.021005 | 0.97873 | 0.36308 | 0.0007859 | 32418.6572 | 0.023682 | 1.6955 | 24.7803 | 28.846 | 0.96946 | 0.087433
2025-02-07 22:48 | 0.34438 | 0.391 | 26.4054 | 0.02107 | 0.97873 | 0.37835 | 0.00081895 | 33781.9792 | 0.023682 | 1.6955 | 25.6739 | 29.886 | 1.0113 | 0.091205
2025-02-07 22:49 | 0.33164 | 0.37653 | 26.405 | 0.021129 | 0.97873 | 0.36436 | 0.00078865 | 32532.1217 | 0.023682 | 1.6955 | 24.8549 | 28.9323 | 0.97841 | 0.08824
2025-02-07 22:50 | 0.31929 | 0.3625 | 26.4045 | 0.020953 | 0.97874 | 0.35078 | 0.00075927 | 31320.1393 | 0.023683 | 1.6955 | 24.0566 | 28.0027 | 0.93581 | 0.084399
2025-02-07 22:51 | 0.31157 | 0.35373 | 26.4039 | 0.021037 | 0.97874 | 0.3423 | 0.00074091 | 30562.5991 | 0.023683 | 1.6954 | 23.5554 | 27.4189 | 0.91793 | 0.082786
2025-02-07 22:52 | 0.32161 | 0.36513 | 26.4033 | 0.021048 | 0.97874 | 0.35333 | 0.00076478 | 31547.158 | 0.023683 | 1.6954 | 24.2066 | 28.1765 | 0.94653 | 0.085365
2025-02-07 22:53 | 0.31852 | 0.36162 | 26.4026 | 0.021048 | 0.97874 | 0.34993 | 0.00075743 | 31244.0746 | 0.023684 | 1.6954 | 24.0065 | 27.9432 | 0.93786 | 0.084583
2025-02-07 22:54 | 0.30076 | 0.34146 | 26.402 | 0.021048 | 0.97874 | 0.33042 | 0.0007152 | 29501.8773 | 0.023684 | 1.6953 | 22.8508 | 26.5975 | 0.88801 | 0.080088
2025-02-07 22:55 | 0.30462 | 0.34584 | 26.4013 | 0.021048 | 0.97874 | 0.33466 | 0.00072438 | 29880.4822 | 0.023685 | 1.6953 | 23.1028 | 26.8904 | 0.89884 | 0.081064
2025-02-07 22:56 | 0.32701 | 0.37126 | 26.4003 | 0.021048 | 0.97874 | 0.35927 | 0.00077763 | 32076.8461 | 0.023685 | 1.6953 | 24.556 | 28.5813 | 0.96157 | 0.086722
2025-02-07 22:57 | 0.32431 | 0.36819 | 26.3992 | 0.021065 | 0.97875 | 0.3563 | 0.00077121 | 31811.5636 | 0.023686 | 1.6952 | 24.3814 | 28.3773 | 0.95475 | 0.086106
2025-02-07 22:58 | 0.31852 | 0.36161 | 26.3981 | 0.02111 | 0.97875 | 0.34993 | 0.00075743 | 31243.3181 | 0.023687 | 1.6952 | 24.0065 | 27.9402 | 0.94052 | 0.084823
2025-02-07 22:59 | 0.30848 | 0.35021 | 26.3971 | 0.021003 | 0.97875 | 0.33891 | 0.00073356 | 30258.504 | 0.023688 | 1.6951 | 23.3544 | 27.1806 | 0.90762 | 0.081856
2025-02-07 23:00 | 0.32701 | 0.37125 | 26.3961 | 0.020948 | 0.97875 | 0.35927 | 0.00077763 | 32076.1251 | 0.023688 | 1.6951 | 24.556 | 28.5784 | 0.95688 | 0.086299
2025-02-07 23:01 | 0.34323 | 0.38966 | 26.3965 | 0.021002 | 0.97875 | 0.37708 | 0.00081619 | 33666.7421 | 0.023688 | 1.6951 | 25.5997 | 29.7933 | 1.0045 | 0.090597
2025-02-07 23:02 | 0.33589 | 0.38133 | 26.3971 | 0.021321 | 0.97875 | 0.36902 | 0.00079875 | 32947.3206 | 0.023688 | 1.6951 | 25.1284 | 29.2453 | 0.99908 | 0.090105
2025-02-07 23:03 | 0.33666 | 0.38221 | 26.3978 | 0.021052 | 0.97875 | 0.36987 | 0.00080059 | 33023.1769 | 0.023687 | 1.6952 | 25.1781 | 29.3035 | 0.98867 | 0.089166
2025-02-07 23:04 | 0.31118 | 0.35328 | 26.3984 | 0.020899 | 0.97875 | 0.34188 | 0.00073999 | 30523.8229 | 0.023687 | 1.6952 | 23.5303 | 27.3861 | 0.9107 | 0.082134
2025-02-07 23:05 | 0.30578 | 0.34715 | 26.399 | 0.020868 | 0.97875 | 0.33594 | 0.00072714 | 29993.7188 | 0.023686 | 1.6952 | 23.1783 | 26.9769 | 0.89431 | 0.080656
2025-02-07 23:06 | 0.31736 | 0.3603 | 26.3985 | 0.021073 | 0.97875 | 0.34866 | 0.00075468 | 31129.772 | 0.023687 | 1.6952 | 23.9314 | 27.8531 | 0.93563 | 0.084382
2025-02-07 23:07 | 0.32778 | 0.37213 | 26.3979 | 0.021121 | 0.97875 | 0.36011 | 0.00077947 | 32152.171 | 0.023687 | 1.6952 | 24.6059 | 28.6377 | 0.96701 | 0.087212
2025-02-07 23:08 | 0.32161 | 0.36512 | 26.3973 | 0.02116 | 0.97875 | 0.35333 | 0.00076478 | 31546.1315 | 0.023688 | 1.6951 | 24.2066 | 28.1725 | 0.95139 | 0.085803
2025-02-07 23:09 | 0.30886 | 0.35065 | 26.3966 | 0.020921 | 0.97875 | 0.33933 | 0.00073448 | 30296.2986 | 0.023688 | 1.6951 | 23.3795 | 27.2095 | 0.90514 | 0.081632
2025-02-07 23:10 | 0.30655 | 0.34802 | 26.396 | 0.020982 | 0.97875 | 0.33679 | 0.00072897 | 30068.9827 | 0.023688 | 1.6951 | 23.2287 | 27.0336 | 0.9013 | 0.081286
2025-02-07 23:11 | 0.32199 | 0.36555 | 26.3961 | 0.020843 | 0.97875 | 0.35375 | 0.0007657 | 31583.8053 | 0.023688 | 1.6951 | 24.2316 | 28.2008 | 0.9382 | 0.084614
2025-02-07 23:12 | 0.31157 | 0.35372 | 26.3963 | 0.021027 | 0.97875 | 0.3423 | 0.00074091 | 30561.3441 | 0.023688 | 1.6951 | 23.5554 | 27.414 | 0.91731 | 0.08273
2025-02-07 23:13 | 0.30616 | 0.34758 | 26.3965 | 0.020876 | 0.97875 | 0.33636 | 0.00072806 | 30031.1945 | 0.023688 | 1.6951 | 23.2035 | 27.0046 | 0.89566 | 0.080778
2025-02-07 23:14 | 0.31427 | 0.35679 | 26.3968 | 0.020857 | 0.97875 | 0.34527 | 0.00074734 | 30826.5073 | 0.023688 | 1.6951 | 23.731 | 27.6186 | 0.91741 | 0.082739
2025-02-07 23:15 | 0.34052 | 0.38659 | 26.397 | 0.020908 | 0.97875 | 0.37411 | 0.00080977 | 33401.7306 | 0.023688 | 1.6951 | 25.4262 | 29.5917 | 0.99258 | 0.089518
2025-02-07 23:16 | 0.33396 | 0.37914 | 26.397 | 0.021104 | 0.97875 | 0.3669 | 0.00079416 | 32757.9397 | 0.023688 | 1.6951 | 25.0042 | 29.1006 | 0.98352 | 0.088701
2025-02-07 23:17 | 0.34361 | 0.3901 | 26.397 | 0.021081 | 0.97875 | 0.37751 | 0.00081711 | 33704.7013 | 0.023688 | 1.6951 | 25.6244 | 29.8224 | 1.0094 | 0.091036
2025-02-07 23:18 | 0.32276 | 0.36643 | 26.397 | 0.021095 | 0.97875 | 0.3546 | 0.00076753 | 31659.6971 | 0.023688 | 1.6951 | 24.2815 | 28.2595 | 0.95172 | 0.085834
2025-02-07 23:19 | 0.30114 | 0.34189 | 26.397 | 0.020785 | 0.97875 | 0.33085 | 0.00071612 | 29538.9514 | 0.023688 | 1.6951 | 22.876 | 26.6237 | 0.87787 | 0.079173
2025-02-07 23:20 | 0.30886 | 0.35065 | 26.397 | 0.02089 | 0.97875 | 0.33933 | 0.00073448 | 30296.3606 | 0.023688 | 1.6951 | 23.3795 | 27.2098 | 0.90382 | 0.081513
2025-02-07 23:21 | 0.32547 | 0.3695 | 26.397 | 0.020905 | 0.97875 | 0.35757 | 0.00077396 | 31924.7897 | 0.023688 | 1.6951 | 24.4563 | 28.4629 | 0.95065 | 0.085737
2025-02-07 23:22 | 0.33357 | 0.3787 | 26.3969 | 0.02093 | 0.97875 | 0.36648 | 0.00079324 | 32720.0616 | 0.023688 | 1.6951 | 24.9793 | 29.0716 | 0.97434 | 0.087874
2025-02-07 23:23 | 0.33357 | 0.3787 | 26.3966 | 0.021045 | 0.97875 | 0.36648 | 0.00079324 | 32719.9937 | 0.023688 | 1.6951 | 24.9793 | 29.0713 | 0.97969 | 0.088355
2025-02-07 23:24 | 0.33743 | 0.38309 | 26.3961 | 0.021058 | 0.97875 | 0.37072 | 0.00080242 | 33098.6155 | 0.023688 | 1.6951 | 25.2278 | 29.3601 | 0.99105 | 0.08938
2025-02-07 23:25 | 0.33319 | 0.37826 | 26.3956 | 0.020945 | 0.97875 | 0.36605 | 0.00079232 | 32681.9619 | 0.023689 | 1.6951 | 24.9545 | 29.0418 | 0.97392 | 0.087836
2025-02-07 23:26 | 0.3274 | 0.37169 | 26.3952 | 0.021037 | 0.97875 | 0.35969 | 0.00077855 | 32113.8295 | 0.023689 | 1.695 | 24.581 | 28.6068 | 0.962 | 0.08676
2025-02-07 23:27 | 0.32855 | 0.373 | 26.3947 | 0.021048 | 0.97876 | 0.36096 | 0.00078131 | 32227.3598 | 0.023689 | 1.695 | 24.6557 | 28.6935 | 0.96573 | 0.087097
2025-02-07 23:28 | 0.32276 | 0.36643 | 26.3943 | 0.021048 | 0.97876 | 0.3546 | 0.00076753 | 31659.2304 | 0.02369 | 1.695 | 24.2815 | 28.2577 | 0.94952 | 0.085635
2025-02-07 23:29 | 0.3413 | 0.38746 | 26.3938 | 0.021031 | 0.97876 | 0.37496 | 0.0008116 | 33476.9034 | 0.02369 | 1.695 | 25.4758 | 29.6472 | 1.0005 | 0.090231
2025-02-07 23:30 | 0.35018 | 0.39754 | 26.3935 | 0.020977 | 0.97876 | 0.38472 | 0.00083272 | 34347.8475 | 0.02369 | 1.695 | 26.0448 | 30.3091 | 1.0226 | 0.092223
2025-02-07 23:31 | 0.35133 | 0.39886 | 26.3932 | 0.021032 | 0.97876 | 0.38599 | 0.00083547 | 34461.3994 | 0.023691 | 1.6949 | 26.1189 | 30.3951 | 1.0285 | 0.092755
2025-02-07 23:32 | 0.35481 | 0.4028 | 26.3929 | 0.021046 | 0.97876 | 0.38981 | 0.00084374 | 34802.1683 | 0.023691 | 1.6949 | 26.3409 | 30.6532 | 1.0388 | 0.093689
2025-02-07 23:33 | 0.35211 | 0.39973 | 26.3926 | 0.021186 | 0.97876 | 0.38684 | 0.00083731 | 34537.024 | 0.023691 | 1.6949 | 26.1682 | 30.4521 | 1.0382 | 0.093628
2025-02-07 23:34 | 0.33666 | 0.3822 | 26.3923 | 0.021037 | 0.97876 | 0.36987 | 0.00080059 | 33022.188 | 0.023691 | 1.6949 | 25.1781 | 29.2997 | 0.98781 | 0.089088
2025-02-07 23:35 | 0.33242 | 0.37738 | 26.392 | 0.020899 | 0.97876 | 0.3652 | 0.00079049 | 32605.5696 | 0.023691 | 1.6949 | 24.9047 | 28.9813 | 0.96954 | 0.08744
2025-02-07 23:36 | 0.36446 | 0.41376 | 26.3915 | 0.020859 | 0.97876 | 0.40041 | 0.00086669 | 35748.6523 | 0.023692 | 1.6949 | 26.956 | 31.368 | 1.0562 | 0.095252
2025-02-07 23:37 | 0.36755 | 0.41726 | 26.3902 | 0.021046 | 0.97876 | 0.4038 | 0.00087403 | 36051.348 | 0.023693 | 1.6948 | 27.1523 | 31.5955 | 1.0742 | 0.096876
2025-02-07 23:38 | 0.36446 | 0.41375 | 26.3887 | 0.021093 | 0.97877 | 0.40041 | 0.00086669 | 35748.0984 | 0.023694 | 1.6947 | 26.956 | 31.3659 | 1.0679 | 0.096314
2025-02-07 23:39 | 0.36948 | 0.41945 | 26.3872 | 0.020898 | 0.97877 | 0.40592 | 0.00087862 | 36240.0925 | 0.023695 | 1.6947 | 27.2749 | 31.7359 | 1.0718 | 0.096665
2025-02-07 23:40 | 0.36523 | 0.41462 | 26.3856 | 0.020798 | 0.97877 | 0.40126 | 0.00086853 | 35823.2416 | 0.023696 | 1.6946 | 27.0051 | 31.4208 | 1.055 | 0.095149
2025-02-07 23:41 | 0.36485 | 0.41418 | 26.3841 | 0.020945 | 0.97878 | 0.40083 | 0.00086761 | 35785.0756 | 0.023697 | 1.6945 | 26.9805 | 31.3911 | 1.0613 | 0.095717
2025-02-07 23:42 | 0.36253 | 0.41155 | 26.3826 | 0.021126 | 0.97878 | 0.39829 | 0.0008621 | 35557.5735 | 0.023698 | 1.6945 | 26.8331 | 31.2184 | 1.064 | 0.095961
2025-02-07 23:43 | 0.35712 | 0.40541 | 26.3812 | 0.020988 | 0.97878 | 0.39235 | 0.00084924 | 35027.1732 | 0.023699 | 1.6944 | 26.4887 | 30.8167 | 1.042 | 0.093978
2025-02-07 23:44 | 0.32662 | 0.37078 | 26.3815 | 0.021007 | 0.97878 | 0.35884 | 0.00077671 | 32035.7118 | 0.023699 | 1.6944 | 24.5311 | 28.5395 | 0.95808 | 0.086407
2025-02-07 23:45 | 0.31234 | 0.35457 | 26.3821 | 0.020897 | 0.97878 | 0.34315 | 0.00074274 | 30634.7292 | 0.023698 | 1.6945 | 23.6056 | 27.4631 | 0.91342 | 0.082379
2025-02-07 23:46 | 0.33628 | 0.38174 | 26.3828 | 0.020981 | 0.97878 | 0.36945 | 0.00079967 | 32982.624 | 0.023698 | 1.6945 | 25.1533 | 29.2642 | 0.98381 | 0.088727
2025-02-07 23:47 | 0.36987 | 0.41988 | 26.3834 | 0.021033 | 0.97878 | 0.40635 | 0.00087954 | 36277.2263 | 0.023697 | 1.6945 | 27.2994 | 31.7616 | 1.0797 | 0.097373
2025-02-07 23:48 | 0.37527 | 0.42601 | 26.3841 | 0.021272 | 0.97878 | 0.41229 | 0.0008924 | 36807.5026 | 0.023697 | 1.6945 | 27.6421 | 32.1608 | 1.1071 | 0.099851
2025-02-07 23:49 | 0.36948 | 0.41944 | 26.3847 | 0.020977 | 0.97878 | 0.40592 | 0.00087862 | 36239.6116 | 0.023696 | 1.6946 | 27.2749 | 31.734 | 1.0758 | 0.097026
2025-02-07 23:50 | 0.36716 | 0.41681 | 26.3853 | 0.020934 | 0.97877 | 0.40338 | 0.00087312 | 36012.5295 | 0.023696 | 1.6946 | 27.1278 | 31.5633 | 1.0672 | 0.09625
2025-02-07 23:51 | 0.35983 | 0.40849 | 26.386 | 0.021003 | 0.97877 | 0.39532 | 0.00085567 | 35293.1595 | 0.023696 | 1.6946 | 26.661 | 31.0207 | 1.0504 | 0.094734
2025-02-07 23:52 | 0.33628 | 0.38175 | 26.3866 | 0.020889 | 0.97877 | 0.36945 | 0.00079967 | 32983.3133 | 0.023695 | 1.6947 | 25.1533 | 29.2669 | 0.97962 | 0.088349
2025-02-07 23:53 | 0.34323 | 0.38964 | 26.3872 | 0.020961 | 0.97877 | 0.37708 | 0.00081619 | 33665.0466 | 0.023695 | 1.6947 | 25.5997 | 29.7867 | 1.0023 | 0.090398
2025-02-07 23:54 | 0.34709 | 0.39402 | 26.3871 | 0.021025 | 0.97877 | 0.38132 | 0.00082537 | 34043.7181 | 0.023695 | 1.6947 | 25.8471 | 30.0746 | 1.0161 | 0.09164
2025-02-07 23:55 | 0.34709 | 0.39402 | 26.3869 | 0.020926 | 0.97877 | 0.38132 | 0.00082537 | 34043.6795 | 0.023695 | 1.6947 | 25.8471 | 30.0744 | 1.0114 | 0.091211
2025-02-07 23:56 | 0.36021 | 0.40893 | 26.3867 | 0.020767 | 0.97877 | 0.39574 | 0.00085659 | 35331.1644 | 0.023695 | 1.6947 | 26.6856 | 31.0499 | 1.0397 | 0.093765
2025-02-07 23:57 | 0.35404 | 0.40191 | 26.3865 | 0.020886 | 0.97877 | 0.38896 | 0.0008419 | 34725.2302 | 0.023695 | 1.6946 | 26.2916 | 30.5912 | 1.0286 | 0.092765
2025-02-07 23:58 | 0.35674 | 0.40498 | 26.3863 | 0.020912 | 0.97877 | 0.39193 | 0.00084833 | 34990.265 | 0.023695 | 1.6946 | 26.4641 | 30.7918 | 1.0373 | 0.093555
2025-02-07 23:59 | 0.34902 | 0.39621 | 26.3859 | 0.020984 | 0.97877 | 0.38344 | 0.00082996 | 34232.8291 | 0.023696 | 1.6946 | 25.9707 | 30.2175 | 1.0194 | 0.091941
After pasting the monitored airflow data, please go to Cell C8 to identify its type:
(1) not normalised Q_A (m3/s), or
(2) normalised Q_A (Nm3/s)
PTprocess is the gas pressure, equal to process presure (Pprocess) minus water vapour pressure

## N2O Emission- Bottom Aeration
Unisense Environment A/S - 2025 ©
Input
Calculations
Constants
| Constant name | Unit | Note | Value | Convert air flow at process temperature
| KHꝊ | mol/L.bar |  | 0.0247 | Choose the air flow type in the Drop down menu
| -ΔsolNH/R | K |  | 2675 | Q_A (Nm3/h) | Nm3/h -DIN 1343 | Air flow in normal cubic meter (STD) | 1000
| CN2O,air | gN/m3 |  | 0.0003 | Q_A [m3/h] | m3/h | Actual air flow rate (V2) | 1073.0276
| R | m3·bar/mol·K |  | 8.314e-05
| kLaNon-aerated process | day-1 | 2-4 day-1 | 3 | There are 2 standards with the same STD pressure and RH=0%, but different temperatures:
| TꝊ | °C | Standard temperature | 25
| Tprocess | °C | Process temperature measured | 15 | DIN 1343 : temperature 273.15K (0°C)
| Pprocess | bar | Pressure in process | 1.013 | ISO 2533 : temperature 288.15K (15°C)
| Aerated zones | Unit | Note | Value
| SN2O concentration | mg N-N2O/L | Nitrous Oxide measured Aerated | 0.5 | In our experience most professionals are using the DIN 1343 but you should always check your own system.
| QA per day (@Tprocess) | m3/day |  | 25752.6626
| QA per second (@ Tprocess) | m3/s |  | 0.29806
| QA per second (@20°C) | m3/s | at 20 deg | 0.30518 | The combined gas law:
| Aerated field size | m2 | Air diffuser cylindrical total area | 462
| DR | m | Depth reactor from diffuser to water level | 7.55
| VR | m3 | Volume of aerated part of the reactor | 3488.1 | Constants - This example will use DIN 1343
| Non-aerated zones | Unit | Note | Value | P1 | bar | Standard - DIN 1343 | 1.013
| SN2O concentration | mg N-N2O/L | Nitrous Oxide measured Non-Aerated | 0.25 | T1 | K | Standard - DIN 1343 | 273.15
| Non-aerated field size | m2 | Total area of non-aeration | 600 | T2 | K | Process temperature | 288.15
| DR,Non-aerated | m | Depth reactor | 5.2
| VR,Non-aerated | m3 | Volume of non-aerated part of the reactor | 3120 | For P2 you will have to consider the water vaper pressure, which is temperature dependent.
Formula | Variables on T and air flow | Unit | Note | Value | Campbells equation:
4.2 | KH | mol/L.bar | Henrys constant at the std. Temp. | 0.033723
4.1 | HN2O,Tprocess | dimensionless | Henrys constant | 1.2378 | The combined gas law including Campbells equation
1.1 | Vg | m3/m2/s | Gas velocity | 0.00066056
1.3 | KLaN2O 20°C | day-1 | Mass transfer coefficient at std. Temp | 21.3411
1.4 | KLaN2O Tprocess | day-1 | Mass transfer coefficient at process Temp | 18.9547
Formula | Aerated zone |  |  |  | Water vapor pressure | mbar | Tprocess | 17.0995
2 | rN2O,Tprocess | gN-N2O/m3/day | N2O emission rate | 3.9951 | P2 (@ Tprocess) | bar | Tprocess | 0.9959
| Emission | KgN-N2O/day | N2O emission rate | 13.9354 | Water vapor pressure | mbar | T20°C | 23.4428
[5 empty] | P2 (@20°C) | bar | T20°C | 0.98956
Formula | Non-aerated zone
3 | rN2O,Tprocess | gN-N2O/m3/day | N2O emission rate | 0.74927
| Emission | kgN-N2O/day | N2O emission rate | 2.3377
|  | Total tank emission | kgN-N2O/day | 16.2731
Calculation example on converting N2O emission to CO2-eq
You should now sum up your emission rate using e.g. numerical integration.
|  | Total emission | kgN-N2O | 50.6
Constants
|  | IPCC | kg CO2-eq pr. kg N2O | 273
|  | Atomic mass Nitrogen | mol/L | 14
|  | Atomic mass Oxygen | mol/L | 16
The N2O sensor is measuring the nitrogen in N2O, why you have to calculate the weight of the total molecule N2O.
|  | Weight of N2O molecule | kg-N2O | 79.5143
|  | CO2 equivalent | kg CO2-eq | 21707.4
𝑃_1∗𝑉_1/𝑇_1 =𝑃_2∗𝑉_2/𝑇_2 " "
𝑃_𝑤 (𝑇)=𝑒^(52,57−6690,9/(𝑇+273,15)−4,681∗ln⁡(𝑇+273,15) )
𝑉_2=𝑉_1∗𝑃_1/𝑃_(2,𝑝𝑟𝑜𝑐𝑒𝑠𝑠) ∗𝑇_2/𝑇_1 =𝑉_1∗𝑃_1/(𝑃_𝑝𝑟𝑜𝑐𝑒𝑠𝑠−𝑃_𝑊 (𝑇)[𝑏𝑎𝑟] )∗𝑇_2/𝑇_1

## N2O Emission - Surface Aeration
Input
Calculations
Constants
Method 1
| Constant name | Unit | Note | Value
| Tprocess | °C | Process temperature measured | 15
| P | kWh | Power consumption (rotors) | 37.5
| SAE | kgO2/kWh | Standard aeration efficiency | 1.2
| Vaerated | m3 | Volume of process tank | 1250
| CN2OProcess | mgN-N2O/L = gN-N2O/m3 | Nitrous oxide liquid phase concentration | 0.1
| Non-aerated zones | Unit | Note | Value
| CN2O,non-aeratedProcess | mgN-N2O/L = gN-N2O/m3 | Nitrous oxide liquid phase concentration | 0.01
| kLaNon-aerated process | day-1 | 2-4 day-1 | 3
| Non-aerated field size | m2 | Total area of non-aeration | 162
| DR,Non-aerated | m | Depth reactor | 5.5
| VR,Non-aerated | m3 | Volume of non-aerated part of the reactor | 891
| Constant name | Unit | Note | Value
| TꝊ | °C | Standard temperature | 20
| α | (-) | Correction from clean water to process conditions | 0.9
| β | (-) | Change in saturation concentration from clean water to process conditions | 0.95
| F | (-) | Fouling factor, usually 1 for surface aerator rotors | 1
| DN2O | m2/s | Diffusion coefficient | 1.77e-09
| DO2 | m2/s | Diffusion coefficient | 2.12e-09
| CO2Process | mg/L | Oxygen Process Concentration | 1.5
| CO2Sat(20°C) | kg/m3 | Oxygen Saturation Concentration | 0.0090324
| CO2Sat_Tprocess | kgO2/m3 | Oxygen Saturation Concentration | 0.0098651
Formula | Aerated zone
1.4 | SOTR | kgO2/h | Standard oxygen transfer rate | 45
1.5 | AOTR | kgO2/h | Actual Oxygen Transfer Rate | -5936.3761
1.6 | KLaO2 Tprocess | h-1 | Mass transfer coefficient | 3.187 | 76.4887
0.2 | KLaN2O Tprocess | h-1 | Mass transfer coefficient | 2.9121 | 69.8901
0.4 | NTRAerated | gN-N2O/h | N2O Emission rate | 364.011
| Emission | kgN-N2O/day | N2O Emission rate | 8.7363
Formula | Non-erated zone
0.5 | Emission | kgN-N2O/day | N2O Emission rate | 0.02673
| Total tank emission | kgN-N2O/day | N2O Emission rate | 8.763